## Sheet1
Building | Room # | Room # (numeric) | Room Accessed (Y/N) | Location Description | Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[12 empty] | Unit of Measure | Condition
[13 empty] | Good | Fair | Poor
AA | 1018 | 1018 | Y | Mechanical Room | 001 | Floor | Concrete | Concrete | NS | [7 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Wall | Drywall | DWJC | P
[6 empty] | Wall | Plaster | Plaster | Y | C | Y |  | √ |  |  | AA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Plaster | Plaster | Y | C | Y |  |  |  |  | AA-1018-001-19-08-10 | Plaster Ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Piping | Elbows/Fittings | Parging Cement | Y | A-B-C | Y | EA | 51 |  | 2 | AA-017 | Elbows/Fittings | 75 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-017 confirmed ACM all elbows/fittings presumed ACM
[6 empty] | Piping |  | PVC | N
[6 empty] | Mechanical | Boiler | Fibreglass | N | [7 empty] | Fibreglass with textile Jacket
[6 empty] | Mechanical | DWHT |  | N
[6 empty] | Ducts | UD |  | N
[6 empty] | Other | Beam | Fireproofing | Y | C | Y |  | 8ft2 |  | <1ft2 | AA-013 | Spray Fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | Sample AA-013 confirmed ACM all fireproofing presumed ACM.
AA | 1019 | 1019 | Y | V.Burton | 002 | Floor | Tile | Vinyl Floor Tiles | Y | A | N | SF | 161 |  |  | AA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight
[6 empty] | Wall | Plaster | Plaster | P | A | Y | SF | 98% | 2ft2 |  | VAA-1018-002-19-08-10 | Plaster Wall | [7 empty] | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Textured Finish | Texture Finish | P | C |  | SF |  | >1ft2 |  | 9-12-074 | [8 empty] | UNABLE TO LOCATE SAMPLE RESULTS IN SHEETS
[6 empty] | Piping | NF
[6 empty] | Mechanical | NF
[6 empty] | Ducts | NF
[6 empty] | Other | NF
AA | 1022 | 1022 | Y | Dr. G Bassler & Dr. A Otter | 003 | Floor | Tile | Vinyl Floor Tiles | P | A | N | Sf | 161 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Plaster | Plaster | P | A | Y | SF |  | 30ft2 |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Textured Finish | Texture Finish | P | [6 empty] | V9-12-074 | [8 empty] | UNABLE TO LOCATE SAMPLE RESULTS IN SHEETS
[6 empty] | Piping | NF
[6 empty] | Mechanical | NF
[6 empty] | Other | NF
AA | 1023A | 1023A | Y | Financial & Admin Services | 004 | Floor | Tile | Vinyl Floor Tiles | P | A | N |  | 135 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 |  | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Concrete | Concrete | NS | A
[6 empty] | Wall | Plaster | Plaster | Y | A | Y |  |  |  |  | AA-1023A-001-19-08-10 | Remnants debris collected on lay in tiles | 0 | 0 | 0 | 0 | 0 | <0.1 |  | Remnants of plaster on lay in tile
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | N | A | [5 empty] | AA-1007A-001 | 2`x2` acoustic ceiling tile, pinhole with fissure pattern
[6 empty] | Ceiling | Textured Finish | Texture Finish | Y |  | Y |  |  |  |  | AA-1023A-002-19-08-10 | Textured ceiling above t-bar ceiling | 5-10% | 0 | 0 | 0 | 0 | 0 |  | Textured ceiling above t-bar ceiling
[6 empty] | Piping |  | Parging Cement | p | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Quantity unknown, concealed, NS as the material was visually similar to sample AA-017
[6 empty] | Mechanical | NF
[6 empty] | Other |  | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray Fireproofing |  |  |  | 95 |  |  |  | Quantity unknown, concealed, NS as the material was visually similar to sample AA-013
AA | 1023 | 1023 | Y | Financial & Admin Services | 005 | Floor | Tile | Vinyl Floor Tiles | P | A | N |  |  |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Concrete | Concrete | NS | A
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | C | [6 empty] | 2' x 4' acosutic ceiling tile, pinhole
[6 empty] | Ceiling | Plaster | Plaster | P | C | Y |  |  |  |  | VAA-1018-001-19-08-10 | Plaster ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Steel | Steel | NS | C
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 9 |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017
[6 empty] | Mechanical | NF
[6 empty] | Other | Ext. Beam | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray Fireproofing |  |  |  | 95 |  |  |  | Quantity unknown, concealed, NS as the material was visually similar to sample AA-013
AA | 1025 | 1025 | Y | Financial & Admin Services | 006 | Floor | Tile | Vinyl Floor Tiles |  | A | N | SF | 159 |  |  | AA-023 | 12''x12'' Vinyl Floor Tile | [6 empty] | Susan Knight | UNABLE TO LOCATE SAMPLE RESULTS IN SHEETS
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-001-19-08-10 | Plaster ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Piping |  | Parging Cement | P | [15 empty] | No access above ceiling, suspect piping present
[6 empty] | Mechanical | NF
[6 empty] | Other |  | Fireproofing | P | [15 empty] | No access above ceiling, suspect fireproofing present
AA | Fibrous Fireproofing9 | Fibrous Fireproofing9 | Y | Vault | 007 | Floor | Tile | Vinyl Floor Tiles | P | A | N |  | √ |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Concrete | Concrete | NS | A |  |  | √ |  |  |  | poured
[6 empty] | Wall | [9 empty] | AA-1023A-001-24-08-10 | Plaster/texture skim coat on wall | [7 empty] | UNABLE TO LOCATE SAMPLE RESULTS IN SHEETS
[6 empty] | Ceiling | Concrete | Concrete | NS |  |  |  | √ |  |  |  | poured
[6 empty] | Piping | NF
[6 empty] | Mechanical | NF
[6 empty] | Other | NF
AA | 1027 | 1027 | Y | Open Office Research Acc | 008 | Floor | Tile | Vinyl Floor Tiles | P | A | N |  | 494 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Acoustic Tile | Lay-in-tiles | NS | C | [6 empty] | 2'x4' Acoustic ceiling tile
[6 empty] | Ceiling | BH | Plaster | P | C | Y |  | √ |  |  | VAA-1018-001-19-08-10 | Plaster on Bulk Head
[6 empty] | Ceiling | Plaster | Plaster | P | C | Y |  |  |  |  | VAA-1018-001-19-08-10 | Plaster ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  | 4+ |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017
[6 empty] | Mechanical | NF
[6 empty] | Other | Ext. Beam | Steel | NS | C | [6 empty] | Steel
[6 empty] | Other | Ext. Beam | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray Fireproofing | 0 | 0 | 0 | 95 | 0 |  |  | Limited visibility, NS as the material was visually similar to sample AA-013
AA | 1030 | 1030 | Y | Financial & Admin Services Copy Room | 009 | Floor | Tile | Clay Tile | NS | A |  |  | 207 |  |  |  | Clay Tiles | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [5 empty] | AA-1030-001-24-08-10 | Drywall Joint Compound
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | C | [6 empty] | 2'X4' Acoustic ceiling tile, pinhole with fleck | [7 empty] | No descrition provided
[6 empty] | Ducts | UD |  |  | C | [6 empty] | Unidentified duct, not insulated
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray Fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-013
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017
[6 empty] | Piping | UP | [9 empty] | Unidentified pipe, not insulated
AA | 1039 | 1039 | Y | J. Baggs & A. Morgan | 010 | Floor | Tile | Vinyl Floor Tiles | Y | A | N |  |  |  |  | AA-016??? | 12''x12'' Vinyl Floor Tile?? | 75?? | 0 | 0 | 0 | 0 | 0 | Susan Knight | Notes say 12''x12'' but say sample description says 9''x9'' and 75%
[6 empty] | Wall | Concrete | Concrete | NS | A
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Stucco ???? | Plaster | P | A | [5 empty] | 9-12-074
[6 empty] | Piping |  | Parging Cement | P |  | Y |  |  |  |  | VAA-017 | Suspect Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Suspect parging cement, No access
Mechanical
[6 empty] | Other |  | Fireproofing | P |  | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS Srayfireproofing visible from 1037, Visibly similar to sample AA-013
AA | 1038 | 1038 | Y | Finanacial & Admin Ser - Storage | 0Fibrous Fireproofing | Floor | Tile | Vinyl Floor Tiles | Y | A | N | SF | 494 |  |  | AA-016 | 9''x9'' Vinyl floor tile, brown wave | 75???? | 0 | 0 | 0 | 0 | 0 | Susan Knight
[6 empty] | Floor | Tile | Tile mastic | Y | A | N |  |  |  |  | AA-016 | Mastic under 9''x9'' vinyl floor tile, brown wave | 3.5 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Plaster | Plaster | P | A | Y | SF |  | 1 |  | VAA-1018-001-19-08-10 | Plaster ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ducts | UD | Fibreglass |  | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Straight run | Fibreglass |  | C | [6 empty] | Fibreglass straight run insulation
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 9 |  |  | VAA-017 | Parging cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Limited visibiliyy, NS as the material was visually similar to sample AA-017
AA | 1037 | 1037 | Y | Financial & Admin Ser - Storage Rm | 012 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | A
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1023A-001-24-08-10
[6 empty] | Piping | [18 empty] | No access hatch rusted
[6 empty] | Mechanical | [18 empty] | No access hatch rusted
[6 empty] | Other | [18 empty] | No access hatch rusted
AA | 1034 | 1034 | Y | PEDDY & J FISHER | 013 | Floor | Tile | Vinyl Floor Tiles | NS | A | N |  | 206 |  |  |  | 9''X9'' Floor tile | [7 empty] | No descrition provided
[6 empty] | Wall | Plaster | Plaster | P | A | Y | [5 empty] | Plaster wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Stucco | Plaster | Y | C | Y | SF |  | 1 |  | AA-1023A-002-19-08-10 | Stucco ceiling | 5-10 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic Tile | Lay-in-tiles | NS | C |  |  | √ |  |  |  | 2'x2' Acoustic ceiling tile | [7 empty] | No descrition provided
[6 empty] | Ducts | UD | Steel | NS | C | [6 empty] | Steel
[6 empty] | Piping | NF
[6 empty] | Mechanical | NF
AA | 1033 | 1033 | Y | Marketing Office | 014 | Floor | Tile | Vinyl Floor Tiles | P | A | N | SF | 197 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [5 empty] | AA-1033-001-24-08-10 | [8 empty] | UNABLE TO LOCATE SAMPLE RESULTS IN SHEETS
[6 empty] | Wall | Concrete | Plaster | P | A | N |  |  |  |  | VAA-1018-002-19-08-10 | Plaster wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Plaster | Plaster | P | A
[6 empty] | Ceiling | NF | [17 empty] | Previous stucco ceiling removed
[6 empty] | Piping | Elbows/Fittings | Parging Cement | Y | C | Y | Ea | 8 | 1 |  | AA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ducts | UD | Fibreglass | NS | C | [14 empty] | Fibreglass on duct
[6 empty] | Mechanical | NF
[6 empty] | Other | NF
AA | 1033A | 1033A | Y | M. Pickard | 015 | Floor | UN |  | NS | A | [6 empty] | Unidentified flooring | [6 empty] | Susan Knight | Can not determine flooring under carpet
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concete
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | C | [6 empty] | 2'x4' Acoustic ceiling tile, pinhole with fleck | [7 empty] | No description provided
[6 empty] | Piping | [18 empty] | No Access above ceiling
[6 empty] | Mechanical | [18 empty] | No Access above ceiling
[6 empty] | Other | [18 empty] | No Access above ceiling
AA | 1032 | 1032 | Y | J. Hulan/ C. Smith | 016 | Floor | Tile | Vinyl Floor Tiles | P | A | N | SF | 186 |  |  | VAA-001 | 9''X9'' Floor tiles | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Concete
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | C | [6 empty] | 2'X2' Acosutic ceiling tile, pinhole
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 4 |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 |  |  | NS as the material was visually similar to sample AA-017
[6 empty] | Ducts | UD | Steel | NS | C | [6 empty] | Steel
[6 empty] | Mechanical | NF
[6 empty] | Other | NF
AA | 1032A | 1032A | Y | J. Hulan Office |  | Floor | Tile | Vinyl Floor Tiles | P | A | N | SF | 192 |  |  | VAA-001 | 9''X9'' Floor tiles | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[5 empty] | 017 | Piping | Elbows/Fittings | Parging Cement | P | A | Y | EA | 2 |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 |  |  | NS as the material was visually similar to sample AA-017
[6 empty] | Ducts | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | NF
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 7 |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 |  |  | NS as the material was visually similar to sample AA-017
AA | 1031 | 1031 | Y | Conference (Board Room) | 018 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Acoustic Tile |  | NS | [7 empty] | 2'x4' Acoustic ceiling tile, pinhole fleck | [7 empty] | New 2'x4' Acoustic ceiling tile, pinhole fleck
[6 empty] | Ducts | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | NF
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C |  | EA | 10 |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 |  |  | NS as the material was visually similar to sample AA-017
AA | 1029A | 1029A | N ? | Electrical Room (Under Stairs) | 019 | [18 empty] | Susan Knight
AA | 1026 | 1026 | Y | Office | 020 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall Joint Compound | [7 empty] | No description provided
[6 empty] | Ceiling | Textured Finish | Texture Finish | P | A | [5 empty] | V19-12-074 | Textured finish
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Hatch not accessable, no access above ceiling, suspect piping present
AA | 1026A | 1026A | Y | V. Collins Office | 021 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall Joint Compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Textured Finish | Texture Finish | P | A | [5 empty] | AA-1026A-001-25-08-10 | Textured finish | [7 empty] | UNABLE TO LOCATE SAMPLE RESULTS IN SHEETS
[6 empty] | Ceiling | Textured Finish | Texture Finish | P | A | [5 empty] | V19-12-074 | Textured finish
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Hatch not accessable, no access above ceiling, suspect piping present
AA | 1024 | 1024 | Y | Open Office | 022 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall |  |  |  | A | [14 empty] | No information provided
[6 empty] | Wall |  |  |  | A | [14 empty] | No information provided
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | N | B | [5 empty] | AA-1007A-001-31-08-10 | 2'X2' Acoustic ceiling tile, pinhole with fissure
[6 empty] | Ducts | UD |  | NS | C | [6 empty] | Not Insulated duct
[6 empty] | Mechanical | NF
[6 empty] | Piping | [18 empty] | No information provided
AA | 1024A | 1024A | Y | H. Kelly | 023 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Textured Finish | Texture Finish | P | A | [5 empty] | VAA-1026A-001-25-08-10 | Textured finish
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | N | A | [5 empty] | AA-1007A-001-31-08-10 | 2'X2' Acoustic ceiling tile, pinhole with fissure
[6 empty] | Ducts | UD |  | NS | [7 empty] | Not Insulated duct
[6 empty] | Mechanical | Ext. Wall | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-013
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Suspect piping behind ext. wall
AA | 1024B | 1024B | Y | D. Sorenson | 024 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall Joint Compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Textured Finish | Texture Finish | P | A | [5 empty] | VAA-1026A-001-25-08-10 | Textured finish
[6 empty] | Ceiling | Textured Finish | Texture Finish | P | A | [5 empty] | V19-12-074 | Textured finish
[6 empty] | Ducts | UD |  | NS | C | [6 empty] | Not Insulated duct
[6 empty] | Mechanical | Spray | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-013
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017, Suspect piping behind ext. wall
AA | 1024C | 1024C | Y | J. Muzychea | 025 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall Joint Compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Textured Finish | Texture Finish | P | A | [5 empty] | VAA-1026A-001-25-08-10 | Textured finish
[6 empty] | Ceiling | Textured Finish | Texture Finish | P | A | [5 empty] | V19-12-074 | Textured finish
[6 empty] | Ducts | UD |  | NS | C | [6 empty] | Not Insulated duct
[6 empty] | Mechanical | Spray | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-013
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017, Suspect piping behind ext. wall
AA | 1024D | 1024D | Y | Multiple Offices | 026 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall Joint Compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | A | [6 empty] | 2'X2' Acoustic eiling tile, fleck | [7 empty] | No description provided
[6 empty] | Wall | Textured Finish | Texture Finish | P | A | [5 empty] | VAA-1026A-001-25-08-10 | Textured finish
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Mechanical | Spray | Fireproofing | P | C | Y | LF | 40 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-013
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017, Suspect piping behind ext. wall
[6 empty] | Ducts | UD |  |  | C
AA | 1024E | 1024E | Y | P. Morris | 027 | Floor | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | A
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Fixed |  |  | A
[6 empty] | Mechanical | Spray | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | Fixed ceiling, presumed fireproofing - sample AA-013
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Fixed ceiling, presumed piping, AA-017
AA | 1024F/1024G | 1024F/1024G | Y | Copy Room/ Kitchen | 028 | Floor | Tiles | Mechanicaly Fixed Tiles | NS | A |  | SF | 2Fibrous Fireproofing |  |  |  | 12''X12'' Vinyl Tile | [6 empty] | Susan Knight | New 12''x12'' Vinyl floor tile
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | A | [6 empty] | 2'X2' Acoustic ceiling tile | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete wall
[6 empty] | Ceiling | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 2 |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 |  |  | NS as the material was visually similar to sample AA-017
[6 empty] | Ducts | UD |  | NS | [7 empty] | Non insulated ducts
AA | 1021 | 1021 | Y | Break Room | 029 | Floor | Sheet flooring | VSF | NS | A | [6 empty] | Vinyl sheet flooring | [6 empty] | Susan Knight | New Vinyl sheet flooring
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint compound | [7 empty] | No description provided
Wall
[6 empty] | Ceiling | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-001-19-08-10 | Plaster ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Other | Panel | Transite | Y | A | N | SF | 10 |  |  | AA-038 | Transite panels | 25 | 0 | 0 | 0 | 0 | 0 |  | Transite panelling confirmed ACM
[6 empty] | Ducts | UD | Metal | NS | C | [6 empty] | Metal
AA | 1020 | 1020 | Y | Recieving Doors | 030 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Wood | wood | NS | A | [6 empty] | Wood
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Plaster | Plaster |  | A | [5 empty] | AA-1023A-001-24-08-10
[6 empty] | Ceiling | Stucco | Plaster | P | A | Y | ft2 | >1 |  |  | AA-1023A-002-19-08-10 | Stucco ceiling | 5-10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-013
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 3 |  | 1 | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-1023A-002-19-08-10
[6 empty] | Ducts | UD
AA | 1020 A/B | 1020 A/B | N |  | 031 | Floor | [17 empty] | Susan Knight
Wall
Ceiling
Piping
Mechanical
Other
AA | 1017 | 1017 | Y | Mail Room | 032 | Floor | Tile | Vinyl Floor Tiles | NS | A | N | SF |  |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Floor | Tile | Vinyl Floor Tiles | NS | A | N | SF |  |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | C | [5 empty] | VAA1007A-001 | 2'x2' Acoustic ceiling tiles | [7 empty] | NS as the material was visually similar to sample AA-1007A-001
[6 empty] | Ducts | UD | Metal | NS | C
[6 empty] | Piping | NF
[6 empty] | Mechanical | NF
[6 empty] | Ceiling | Plaster | Plaster | P | A | Y |  |  |  |  | AA-1023A-002-19-08-10 | Stucco ceiling | 5-10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-1023A-002-19-08-10, Not painted
AA | 1017A | 1017A | Y | Richard Predham | 033 | Floor | Tile | Vinyl Floor Tiles | NS | A | N | SF | 74 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | Concrete
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | [6 empty] | VAA1007A-001 | 2'x2' Acoustic ceiling tiles | [7 empty] | NS as the material was visually similar to sample AA-1007A-001
[6 empty] | Other | [18 empty] | NO Access above celiling
AA | 1017B | 1017B | Y | D. Ellis | 034 | Floor | Tile | Vinyl Floor Tiles | NS | A | N | SF | 74 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete |  | A | [6 empty] | Concrete
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | C | [5 empty] | VAA1007A-001 | 2'x2' Acoustic ceiling tiles | [7 empty] | NS as the material was visually similar to sample AA-1007A-001
[6 empty] | Other | [18 empty] | NO Access above celiling
AA | 1017C | 1017C | Y | Mail Room | 035 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | C | [5 empty] | VAA1007A-001 | 2'x2' Acoustic ceiling tile | [7 empty] | NS as the material was visually similar to sample AA-1007A-001
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | C | [6 empty] | Parging Cement | [7 empty] | Suspect New
[6 empty] | Ducts | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | NF |  | NS
[6 empty] | Other | NF |  | NS
AA | 1017D | 1017D | Y | Mail Break Room | 036 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint Compound | [7 empty] | Original
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall & Compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tile | Lay-in-tiles | NS | A | [5 empty] | VAA1007A-001 | 2'x2' Acoustic ceiling tile | [7 empty] | NS as the material was visually similar to sample AA-1007A-001
[6 empty] | Ceiling | Concrete | Concrete | NS | C | [6 empty] | poured
[6 empty] | Ducts | UD | Metal | NS | [7 empty] | Metal duct
[6 empty] | Piping | NF
[6 empty] | Mechanical | NF
[6 empty] | Other | NF
AA | 1017E | 1017E | Y | Loading Bay | 037 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Concrete | Concrete | NS | C | [6 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
AA | 1016 | 1016 | Y | Storage Room | 038 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Concrete
[6 empty] | Wall | Plaster | Plaster | P |  | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Duct |  | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | STR |  | NS
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P |  | Y |  |  |  |  | VAA-017 | Parging cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-017
AA | 1016A | 1016A | Y | Female Washroom | 039 | Floor | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles | [6 empty] | Susan Knight
[6 empty] | Wall | Plaster | Plaster | P | A | [6 empty] | Plaster Wall | [7 empty] | Samples collected not on sheet
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles
[6 empty] | Ceiling | Plaster | Plaster | P | A | [6 empty] | Plaster ceiling | [7 empty] | Samples collected not on sheet
[6 empty] | Piping | Elbows/Fittings | Fibreglass | NS | A | [6 empty] | Fibreglass with textile Jacket | [7 empty] | NO Parging
AA | 1015 | 1015 | Y | Male Washroom | 040 | Floor | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles | [6 empty] | Susan Knight
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint Compound
[6 empty] | Ceiling | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-001-19-08-10 | Plaster ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | A | Y |  |  |  |  | VAA-017 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | No access hatch suspect piping present
AA | 1014 | 1014 | Y | File Room | 041 | Floor | Concrete | Concrete | NS | [7 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint Compound
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Ceiling | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Ceiling | Stucco | Plaster | P | [6 empty] | V9-12-074 | Stucco ceiling
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | [7 empty] | 2'x2' Acoustic ceiling tiles | [7 empty] | Pinhole maybe new or visually similar to AA-2014-001-08-09-10
[6 empty] | BH | Stucco |  | NS | [7 empty] | Stucco Bulk Head
[6 empty] | BH | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | [7 empty] | Fibreglass
AA | 1013 | 1013 | Y | English Corridor/Storage | 042 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Concrete | Concrete | NS | C | [6 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | Y | C | Y | EA | 37 |  |  | AA-018019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Piping | STR | Fibreglass | N | B | N |  |  |  |  | AA-1013-001-27-08-10 | Tar paper | [7 empty] | Hatch by water fountain
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | B | Y | EA | 1 |  |  |  | Parging cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Hatch by water fountain, NS as the material was visually similar to AA-018/019
AA | 1013A | 1013A | Y | Jackets Closet | 043 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Concrete | Concrete | NS | C | [6 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 6 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | [18 empty] | Wall hatch, no access
AA | 1013B | 1013B | Y | Dressing Room | 044 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Concrete | Concrete | NS | C | [6 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 24 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0
AA | 1013C | 1013C | Y | Washroom | 045 | Floor | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles | [6 empty] | Susan Knight
[6 empty] | Wall | Plaster | Plaster | P | A |  | SF |  |  | 20 |  | Plaster | [7 empty] | Not Containing, all plaster presumed ACM.
[6 empty] | Wall | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles
[6 empty] | Ceiling | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | A | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Duct | NF
[6 empty] | Mechanical | NF
[6 empty] | Other | NF | [17 empty] | Suspect Piping behind wall
AA | 1013D | 1013D | Y | Corridor/Electrical Cage | 046 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 17 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019
[6 empty] | Other | [18 empty] | Electrical Equipment Present
AA | 1013E | 1013E | Y | Dressing Room # 2 | 047 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Concrete | Concrete | NS | C | [6 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | B/C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P |  | Y | EA | 26 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019
AA | 1013F | 1013F | Y | Washroom | 048 | Floor | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles | [6 empty] | Susan Knight | As per location 045
[6 empty] | Wall | Plaster | Plaster | P | A | [6 empty] | Plaster | [7 empty] | As per location 045, Not Containing, all plaster presumed ACM.
[6 empty] | Wall | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles | [7 empty] | As per location 045
[6 empty] | Ceiling | Concrete | Concrete | NS | A | [6 empty] | poured | [7 empty] | As per location 045
[6 empty] | Piping | STR | Fibreglass | NS | A | [6 empty] | Fibreglass with textile Jacket | [7 empty] | As per location 045
[6 empty] | Duct | NF | [17 empty] | As per location 045
[6 empty] | Mechanical | NF | [17 empty] | As per location 045
[6 empty] | Other | NF | [17 empty] | As per location 045, Suspect Piping behind wall
AA | 1013G | 1013G | Y | Mechanical Room | 049 | Floor | Concrete | Concrete | NS | [7 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | poured and precast
[6 empty] | Ceiling | Concrete | Concrete | NS | [7 empty] | poured
[6 empty] | Piping | STR | Fibreglass | NS | A | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | A | Y | EA | 29 |  | 3 | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019
[6 empty] | Duct | UD | Parging Cement | P | A | Y | EA | 120 |  | 10SF | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019
[6 empty] | Duct | EXP | Cloth |  | A | [5 empty] | AA-1013F-001-27-08-10 ??
[6 empty] | Other | [18 empty] | Residual parging on old pipe in ceiloing, multiple sections of duct work needs to be lagged/repaired
AA | 1012 | 1012 | Y | Labour Storage Room | 050 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'x4' Acoustic ceiling tile | [7 empty] | New
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint comound | [7 empty] | No description provided
[6 empty] | Piping | STR | Fibreglass | NS | [7 empty] | Fibreglass
[6 empty] | Piping | Elbows/Fittings | [17 empty] | Appears parging may have been removed can not get close enough to see
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P |  | Y | EA |  |  | 9 | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Suspect reminant, NS as the material was visually similar to AA-018/019
[6 empty] | Duct | UD | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
Other
AA | 10Fibrous FireproofingA | 10Fibrous FireproofingA | Y | Group Telecom | 051 | Floor | Concrete | Concrete | NS | A | [6 empty] | poured | [6 empty] | Susan Knight
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint comound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'x4' Acoustic ceiling tile | [7 empty] | New
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 1 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019, possibly more present
[6 empty] | Duct | UD | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
AA | 1008 | 1008 | Y | Utilities Closet | 052 | Floor | Tile | Clay Tile | NS | A | [6 empty] | Clay Tiles | [6 empty] | Susan Knight
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-001-19-08-10 | Plaster ceiling | 1-5 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1018-001-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Piping | STR |  | NS | A | [6 empty] | Not Insulated
[6 empty] | Piping | Elbows/Fittings |  | NS | A | [6 empty] | Not Insulated
[6 empty] | Mechanical | UD | Metal | NS | B/C | [6 empty] | Metal
AA | 1047 | 1047 | Y | Electrical Closet | 053 | Floor | Tile | Vinyl Floor Tiles | NS | A | [6 empty] | 12''X12'' Vinyl Floor Tile | [6 empty] | Susan Knight | New
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Drywall & Compound | DWJC | P | [6 empty] | AA-028?? | Drywall Joint Compound | [7 empty] | No description provided
AA | 1004 | 1004 | Y | Financial & Admin Budgets Services | 054 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | 244 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | NEW
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | N | C | [5 empty] | AA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Wall | Plaster | Plaster | P | C | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM. Under new drywall
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | C | 3 | [5 empty] | Parging cement | [7 empty] | Appears New
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | 1004 E | Closet
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint compound
[6 empty] | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf |  |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0
AA | 1004D | 1004D | Y | Office - Budgeting | 055 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | 91 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | Over original walls
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | B | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | New | [17 empty] | New
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass with textile Jacket
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 1 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019, Maybe new
AA | 1004C | 1004C | Y | L. Pike | 056 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | 185 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound
[6 empty] | Wall | Texture Skim Coat | Texture Finish | P | A | [5 empty] | AA- ???? | Textured Skim Coat
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | UD | Fibreglass | NS | C | [6 empty] | Fibreglass
[6 empty] | Piping | STR | Fibreglass | NS | CC | [6 empty] | Fibreglass
[6 empty] | Mechanical | BM | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-013
AA | 1004B | 1004B | Y | S. Kelly | 057 | Floor | Tile | Vinyl Floor Tiles | P | A | N | Sf | Fibrous Fireproofing2 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | New
[6 empty] | Wall | Texture Skim Coat | Texture Finish | P | A | [5 empty] | AA- 1026A-001-24-08-10 | Textured Skim Coat
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | UD | Plastic | NS | C | [6 empty] | Plastic
[6 empty] | Mechanical | SF | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | Can not access space, NS as the material was visually similar to sample AA-013
AA | 1004A | 1004A | Y |  | 058 | Floor | Tile | Vinyl Floor Tiles | P | A | N | Sf | Fibrous Fireproofing8 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | AS per Loc. 057, NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | New
[6 empty] | Wall | Texture Skim Coat | Texture Finish | P | A | [5 empty] | AA- 1026A-001-24-08-10 | Textured Skim Coat
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | UD | Plastic | NS | C | [6 empty] | Plastic
[6 empty] | Mechanical | SF | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | As per Loc. 057, NS as the material was visually similar to sample AA-013
AA | 1004F | 1004F | Y | Board Room | 059 | Floor | Tile | Vinyl Floor Tiles | P | A | N | Sf | 134 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | AS per Loc. 057, NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | New
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | UD | Plastic | NS | C | [6 empty] | Plastic
[6 empty] | Mechanical | SF | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | As per Loc. 057, NS as the material was visually similar to sample AA-013
AA | 1002 | 1002 | Y | Student Recruitment | 060 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | Fibrous Fireproofing8 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | UD | Fibreglass | NS | C | [6 empty] | Fibreglass and uninulsted straight piping
[6 empty] | Piping | NF
[6 empty] | Mechanical | NF
[6 empty] | Other | NF
AA | 1002A | 1002A | Y | Office | 061 | Floor | Tile | Vinyl Floor Tiles | P | A | N | Sf | 203 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Piping | Spray | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | Suspect Fireproofing
[6 empty] | Mechanical | Elbows/Fittings | Parging Cement | P | C | Y |  |  |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Suspect Piping
[6 empty] | Duct | [18 empty] | Suspect Duct
AA | 1002B | 1002B | Y | Office | 062 | Floor | Tile | Vinyl Floor Tiles | P | A | N | Sf | 109 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | UD | Fibreglass | NS | C | [6 empty] | Fibreglass and uninsulated ducts
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass on straight pipe
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 9 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019
[6 empty] | SP | Spray | Fireproofing | P | C | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
AA | 1002C | 1002C | Y | Office | 063 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | Fibrous Fireproofing3 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Duct | UD | Fibreglass | NS | C
[6 empty] | Piping | NF | [17 empty] | Suspect piping behind walls
AA | 1002 D | 1002 D | Y | Storage | 064 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | 25 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Piping | NF
[6 empty] | Duct | NF
[6 empty] | Mechanical | NF
[6 empty] | Other | NF
AA | 1000 (A-H) | 1000 (A-H) | Y | Office of Student Recrutiment | 065 | Floor | Tile | Vinyl Floor Tiles | P | A | N | SF | Fibrous Fireproofing85 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Stuuco | Plaster |  | C | [5 empty] | V9-12-072???
[6 empty] | Duct |  | Fibreglass | NS | C | [6 empty] | Fibreglass and uninsulated ducts
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P |  | Y | EA |  |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | No access above ceiling Suspect piping
[6 empty] | Mechanical | Spray | Fireproofing | P |  | Y |  |  |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | No access above ceiling Suspect Fireproofing
AA | 1001 | 1001 | Y | CIAP | 066 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | 392 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Wall | Plaster | Plaster | P | C | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Piping | [18 empty] | Suspect piping behind walls of heaters
AA | 1001A | 1001A | Y | Financial Reporting & Analysis | 067 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | 812 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass and uninsulated ducts
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 5 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to AA-018/019
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 8 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
[6 empty] | Duct | UD | Fibreglass | NS | C | [6 empty] | Fibreglass ducts
AA | 1001A | 1001A | Y |  | 068 | Floor | Tile | Vinyl Floor Tiles | Y | B | [5 empty] | AA-012 | 12X12 Vinyl floor tile | 6.5 | 0 | 0 | 0 | 0 | 0 | Susan Knight
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Plaster | Plaster | P |  | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | BH | Plaster | P |  | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Stucco | Plaster | P | C | [14 empty] | No access hatch I ceiling only in bulkhead
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 5 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | Suspect piping in bulkhead, NS as the material was visually similar to AA-018/019
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 8 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | Suspect fireproofing in bulkhead NS as the material was visually similar to sample AA-0013
AA | 1001B | 1001B | Y | Kitchenet | 069 | Floor | Tile | Vinyl Floor Tiles | P | A |  | SF | 29 |  |  | VAA-012 | 12X12 Vinyl floor tile | 6.5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-0012
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Stucco | Plaster | P | C | [5 empty] | V09-12-074 ???
AA | 1001C | 1001C | Y | Office | 070 | Floor | Tile | Vinyl Floor Tiles | P | B | N | Sf | 125 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Plaster | Plaster | P | A | Y |  |  |  |  | VAA-1018-002-19-08-10 | Plaster Wall | <0.1 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
[6 empty] | Duct | UD | Fibreglass | NS | C | [6 empty] | Fibreglass
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 2 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-018/19, Maybe new
AA | 1003 | 1003 | Y | Office | 071 | Floor | Tile | Vinyl Floor Tiles | P | A | N | Sf | 125 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-006 | 2'X4' Acoustic Ceiling Tile, Pinhole fleck
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 30 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping | [7 empty] | Suspect piping behind ext. wall
AA | 1005 | 1005 | Y | Paul Chancey | 072 | Floor | Tile | Vinyl Floor Tiles | NS | B |  |  | 170 |  |  |  | Suspect Vinyl floor tile | [6 empty] | Susan Knight | Suspect Floor Tile
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'X2' Acoustic Ceiling Tile, Pinhole fissure
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping
AA | 1005B | 1005B | Y | Office | 073 | Floor | Tile | Vinyl Floor Tiles | NS | B |  |  | 160 |  |  |  | Suspect Vinyl floor tile | [6 empty] | Susan Knight | Suspect Floor Tile
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'X2' Acoustic Ceiling Tile, Pinhole fissure
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping
AA | 1005A | 1005A | Y | Copy Room | 074 | Floor | Tile | Vinyl Floor Tiles | NS | B |  |  | 86 |  |  |  | Suspect Vinyl floor tile | [6 empty] | Susan Knight | Suspect Floor Tile, As per location 073
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete | [7 empty] | As per location 073
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided, As per location 073
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM , As per location 073
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'X2' Acoustic Ceiling Tile, Pinhole fissure | [7 empty] | As per location 073
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 16 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping
AA | 1007A | 1007A | Y | P. Chancey | 075 | Floor | Tile | Vinyl Floor Tiles | NS | B |  |  | 242 |  |  |  | Suspect Vinyl floor tile | [6 empty] | Susan Knight | Suspect Floor Tile
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | No description provided
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete | [7 empty] | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'X2' Acoustic Ceiling Tile, Pinhole fissure
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 35 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping | [7 empty] | Suspect piping behind wall - heater
AA | 1007 | 1007 | Y |  | 076 | Floor | Tile | Vinyl Floor Tiles | P | B |  |  | 155 |  |  | VAA-001 | 9'X9' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-1007A-001-31-08-10 | 2'X2' Acoustic Ceiling Tile, Pinhole fissure
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal | [7 empty] | As per location 074
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013, As per location 074
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping | [7 empty] | As per location 074
AA | 1009 | 1009 | Y | CIAP K. Muiick | 077 | Floor | Tile | Vinyl Floor Tiles | NS | B |  |  | 165 |  |  |  | Suspect Vinyl floor tile | [6 empty] | Susan Knight | Suspect Floor Tile
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | Appears to be original drywall
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-1007A-001-31-08-10 | 2'X2' Acoustic Ceiling Tile, Pinhole fissure
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal | [7 empty] | As per location 074
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 20 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013, As per location 074
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping | [7 empty] | As per location 074
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 3 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-0018/019
AA | 1010 | 1010 | Y | DR. M. Baker | 078 | Floor | Tile | Vinyl Floor Tiles | P | B |  |  | 133 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [5 empty] | VAA-1007A-001-31-08-10 | 2'X2' Acoustic Ceiling Tile, Pinhole fissure
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal | [7 empty] | As per location 077
[6 empty] | Mechanical | Ext. Beam | Fireproofing | P | C | Y | LF | 16 |  |  | VAA-013 | Spray fireproofing | 0 | 0 | 0 | 95 | 0 | 0 |  | NS as the material was visually similar to sample AA-0013, As per location 077
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Straight fibreglass piping | [7 empty] | As per location 077
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 3 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-0018/019, As per location 077
| 10Fibrous Fireproofing | 10Fibrous Fireproofing | N - View from window in doorway | Group Telecom | 079 | Floor | Tile | Vinyl Floor Tiles | P | A |  |  | 134 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Wood | wood | NS | A | [6 empty] | Wood | [7 empty] | Sample AA-1018-002-19-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Wall | Plaster | Plaster | P | A | [5 empty] | VAA-1026A-001 | Plaster Wall | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Ceiling | Stucco | Plaster | P | C | [5 empty] | V09-12-074
[6 empty] | Piping | [10 empty] | Suspect piping | [7 empty] | No access to room suspect piping behind walls
[6 empty] | Mechanical | [10 empty] | Suspect fireproofing | [7 empty] | No access to room suspect fireproofing behind bulkheads
AA | 1C01 East Wing | 1C01 East Wing | Y |  | 080 | Floor | Tile | Vinyl Floor Tiles | P | A | [5 empty] | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | Concrete
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | B | [6 empty] | 2'X4' Acoustic Ceiling Tile, Pinhole with fleck
[6 empty] | BH | Above Doors | Transite | Y | A |  | sf | 10 |  |  | AA-038 | Transite Sheeting | 25 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-038 confirmed ACM all transite presumed ACM.
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | B | [6 empty] | 2'x'4 Acoustic ceiling tile, pinhole with fleck
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | B | [6 empty] | 2'x4' Acoustic ceiling tile, pinhole
[6 empty] | Wall Ceiling | BH | Plaster | Y | C |  | SF |  | >2 |  | AA-1C01-001-31-08-10 | Plaster on wire mesh | <0.1 | 0 | 0 | 0 | 0 | <0.1 |  | Sample AA-1C01-001-31-08-10 confirmed ACM all plaster presumed ACM.
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass piping
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 8+ |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-0018/019
[6 empty] | duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Mechanical | NF
[6 empty] | Other | NF | [17 empty] | Limited access above t-bar - multiple conduit and piping systems present
AA | 1C01 West Wing | 1C01 West Wing | Y |  | 080 | Floor | Tile | Vinyl Floor Tiles | P | A | [5 empty] | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Wall | Concrete | Concrete | NS | [7 empty] | Concrete
[6 empty] | Wall |  | Transite | P |  |  | sf | 4 |  |  | VAA-038 | Transite Sheeting | 25 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-038 confirmed ACM all transite presumed ACM.
[6 empty] | Wall | Drywall & Compound | DWJC | P | [7 empty] | Drywall joint compound | [7 empty] | No description provided
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'x4' Acoustic ceiling tile, pinhole
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'x'4 Acoustic ceiling tile, pinhole with fleck
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'x'4 Acoustic ceiling tile, pinhole with fissure
[6 empty] | Ceiling | Stucco | Plaster | P | C | [5 empty] | V09-12-074
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass piping
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA |  |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-0018/019
4 Elbows in vicinity of AA1018, 17 elbows in vicinity AA1027
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | BH |  | Plaster | Y | C |  | SF | UK |  |  | VAA-1C01-001-31-08-10 | Plaster on wire mesh | <0.1 | 0 | 0 | 0 | 0 | <0.1 |  | NS as the material was visually similar to sample AA-1C01-001-31-08-10
AA | 1C10 North Wing | 1C01 North Wing | Y |  | 080 | Floor | Tile | Vinyl Floor Tiles | P | A | N | SF | 224 |  |  | VAA-001 | 9''X9'' Vinyl floor tile | 4.8 | 0 | 0 | 0 | 0 | 0 | Susan Knight | NS as the material was visually similar to sample AA-001
[6 empty] | Floor | Sheet flooring | VSF | NS | A | [6 empty] | Green vinyl sheet flooring | [7 empty] | New green vinyl sheet flooring
[6 empty] | Floor | Sheet flooring | VSF | NS | A | [6 empty] | Black vinyl sheet flooring | [7 empty] | New black vinyl sheet flooring
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | Concrete
[6 empty] | Wall | Drywall & Compound | DWJC | P | A | [6 empty] | Old Drywall joint compound
[6 empty] | Wall | Concrete | Concrete | NS | A | [6 empty] | poured
[6 empty] | Ceiling | Concrete | Concrete | NS | C | [6 empty] | poured
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'x'4 Acoustic ceiling tile, pinhole fleck, new | [7 empty] | New 2'x4' Acoustic ceiling tile, pinhole fleck
[6 empty] | Piping | STR | Fibreglass | NS | A,B,C | [6 empty] | Fibreglass with TEX. JKT
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | A,B,C | Y | EA | 70 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-0018/019
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal
[6 empty] | Ceiling | Acoustic tiles | Lay-in-tiles | NS | C | [6 empty] | 2'x'2 Acoustic ceiling tile, pinhole Fissure | [7 empty] | Old 2'x2' Acoustic ceiling tile, pinhole fissure
[6 empty] | BH | Drywall & Compound | DWJC | N | B | [5 empty] | AA1C01-01 | New drywall joint compond | 0 | 0 | 0 | 0 | 0 | 0 |  | New drywall joint compond
[6 empty] | BH | Drywall & Compound | DWJC | Y | B | [5 empty] | AA1C01-02 | Old drywall joint compond | 5 | 0 | 0 | 0 | 0 | 0 |  | Sample AA-1C01-02 confirmed ACM all DWJC presumed ACM.
[6 empty] | Piping | STR | Fibreglass | NS | C | [6 empty] | Fibreglass with TEX. JKT
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | C | Y | EA | 9 |  |  | VAA-018/019 | Parging Cement | 75 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to sample AA-0018/019
[6 empty] | Duct | UD | Metal | NS | C | [6 empty] | Metal