## Part 1
Building | Room # | Room # (numeric) | Room Accessed (Y/N) | Location Description | PLEL Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[12 empty] | Unit of Measure | Condition
[13 empty] | Good | Fair | Poor
AQ | 1003B | 1003 | Y | Mechanical Room | 001 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | N | [6 empty] | S001 | Parging Cement
[6 empty] | Mechanical | Tank | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
AQ | 1003C | 1003 | Y | Electrical Room | 002 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 1003A | 1003 | Y | Office | 003 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS001 | Parging Cement | [7 empty] | NS as the material is new.
[6 empty] | Mechanical | Tank | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
AQ | 1003, 1003E, 1003F, 1003D, 1S06, 1005 | 1003 | Y | Office | 004 | Floor | [17 empty] | PLEL
Wall
Ceiling
Piping
Mechanical
[6 empty] | Other | [18 empty] | No sampling as this room underwent 100% renovations within the past 16 years.
AQ | 1002C, 1004, 1002D, 1C02, 1C04, 1002, 1005A | 1002 | Y | Office | 005 | Floor | [17 empty] | PLEL
Wall
Ceiling
Piping
Mechanical
[6 empty] | Other | [18 empty] | No sampling as this room underwent 100% renovations within the past 16 years.
AQ | 1C01 |  | Y | Hallway | 006 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in Drywall Tile | NS | [15 empty] | NS as the material is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 1001 | 1001 | Y | Main Ventilation | 007 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS001 | Parging Cement | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AQ | 1000, 1000A | 1000 | Y | Fitness | 008 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1000 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S002 | 2' x 4' pinhole fissure
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS001 | Parging Cement | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 1V01 |  | Y | Corridor | 009 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 1S01 |  | Y | Stairwell | 010 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S004 | 2' x 4' pinhole fleck
[6 empty] | Piping | Straight Run | Insulation | Y | D | Y | SF | - | 1 | 1 | S003 | Straight Pipe Insulation | 10 | 0 | 0 | 20 | 0 | 0
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2000, 2004 | 2000 2004 | Y | Main Lobby | 011 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2500 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S007 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S006 | 2' x 2' pinhole fissure
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 2500 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S005 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2007 | 2007 | Y | Male Changeroom | 012 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | Y | A | N | Sf | 120 | - | - | S008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2006 | 2006 | Y | Female Change | 013 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | Y | A | N | SF | 200 | - | - | S009 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ |  |  | Y | Storage Room by Tim's (New, no room #) | 014 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S010 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AQ | 2007A | 2007 | Y | Male Changeroom | 015 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2C03 |  | Y | Hallway | 016 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S004
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2007B | 2007 | Y | Office | 017 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2008 | 2008 | Y | Janitor's Closet | 018 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ |  |  | Y | "Balkony" next to Tim's (no room #) | 019 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2001 | 2001 | Y | Office | 020 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
AQ | 2S01 |  | Y | Under 2S01 | 020A | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
AQ | 2010 | 2010 | Y | Office | 021 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Other | N/F
AQ | 2011, 2011A | 2011 | Y | Office | 022 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as the material is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S011 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
AQ | 2016, 2016A, 2V02 | 2016 | Y | Office | 023 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as the material is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 575 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 575 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S013 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
AQ | 2017A | 2017 | Y | Office | 024 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2017B | 2017 | Y | Office | 025 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2017 | 2017 | Y | Office | 026 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2018 | 2018 | Y | Office | 027 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2019 | 2019 | Y | Office | 028 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AQ | 2020A | 2020 | Y | Office | 029 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S014 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AQ | 3020 | 3020 | Y | Office | 030 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3022 | 3022 | Y | Office | 031 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3023 | 3023 | Y | Office | 032 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | Y | A | N | SF | 14 | - | - | S015 | Transite | 20 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3021 | 3021 | Y | Office | 033 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | P | A | N | SF | 14 | - | - | VS015 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S015.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3019 | 3019 | Y | Office | 034 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | P | A | N | SF | 14 | - | - | VS015 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S015.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3018 | 3018 | Y | Office | 035 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | P | A | N | SF | 14 | - | - | VS015 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S015.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3017 | 3017 | Y | Office | 036 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | P | A | N | SF | 14 | - | - | VS015 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S015.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3014 | 3014 | Y | Office | 037 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | P | A | N | SF | 14 | - | - | VS015 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S015.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3024 | 3024 | Y | Office | 038 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3016 | 3016 | Y | Office | 039 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 10 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3015, 3015A | 3015 | Y | Office | 040 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as the material is new.
[6 empty] | Ceiling | Drywall | DWJC | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f | [17 empty] | No access above ceiling.
AQ | 2012 | 2012 | Y | Office | 041 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2013A | 2013 | Y | Office | 042 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2014 | 2014 | Y | Office | 043 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 380 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2021 | 2021 | Y | Office | 044 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2022 | 2022 | Y | Office | 045 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S016 | 2' x 4' longitudinal fissure and pinhole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2023 | 2023 | Y | Office | 046 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AQ | 3003 | 3003 | Y | Office | 047 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3003A | 3003 | Y | Office | 048 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3002 | 3002 | Y | Office | 049 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3001 | 3001 | Y | Office | 051 | Floor | Tile | Vinyl tile | N | [6 empty] | S017 | 12' x 12' Grey with abundant grey flecks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S017 | 12' x 12' Grey with abundant grey flecks
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3004 | 3004 | Y | Ladies Washroom | 052 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3005 | 3005 | Y | Mens Washroom | 053 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3008 | 3008 | Y | Fitness Area | 054 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' pinhole fissure | [7 empty] | NS as the material Was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3006, 3006A, 3006B | 3006 | Y | Office | 055 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 300 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S004.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ |  |  | Y | Attic (no room #) | 056 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3007 | 3007 | Y | Office | 057 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3009 | 3009 | Y | Office | 058 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f | [17 empty] | No access above ceiling.
AQ | 3010 | 3010 | Y | Office | 059 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f | [17 empty] | No access above ceiling.
AQ | 3011 | 3011 | Y | Office | 060 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3012 | 3012 | Y | Office | 061 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3013 | 3013 | Y | Office | 062 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | P | A | N | SF | 28 | - | - | VS015 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S015.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2009, 2009A, 2009B | 2009 | Y | Office | 063 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Panel | Transite | P | A | N | SF | 28 | - | - | VS015 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S015.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3C01 |  | Y | Hallway | 064 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS017 | 12' x 12' Grey with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S017
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS017 | 12' x 12' Grey with abundant grey flecks | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3C03 |  | Y | Hallway | 065 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2002 | 2002 | Y | Womens' washroom | 066 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2003 | 2003 | Y | Mens Washroom | 067 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F

## Part 2
Building | Room # | Room # (numeric) | Room Accessed (Y/N) | Location Description | PLEL Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[12 empty] | Unit of Measure | Condition
[13 empty] | Good | Fair | Poor
AQ | 2C02 |  | Y | corridor |  | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2V03 |  | Y | vestribule |  | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2025 |  | Y |  |  | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2S05 |  | Y | Stairwell |  | Floor |  | Rubber | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 1002A, 1002B | 1002 | Y | Office | 005 | Floor | [10 empty] | New | [6 empty] | PLEL
[6 empty] | Wall | [10 empty] | New
[6 empty] | Ceiling | [10 empty] | New
[6 empty] | Piping | [10 empty] | New
[6 empty] | Mechanical | [10 empty] | New
[6 empty] | Other | [10 empty] | New | [7 empty] | No sampling as this room underwent 100% renovations within the past 16 years.
AQ | 1C03, 1C04 |  | Y | corridor | 005 | Floor | [10 empty] | New | [6 empty] | PLEL
[6 empty] | Wall | [10 empty] | New
[6 empty] | Ceiling | [10 empty] | New
[6 empty] | Piping | [10 empty] | New
[6 empty] | Mechanical | [10 empty] | New
[6 empty] | Other | [10 empty] | New | [7 empty] | No sampling as this room underwent 100% renovations within the past 16 years.
AQ | 1S02 |  | Y | Stairwell | 005 | Floor | N/F | [16 empty] | PLEL
[6 empty] | Wall | N/F
[6 empty] | Ceiling | N/F
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | Steel sprial staircase
AQ | 2V01 |  | Y | vestibule | 010 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' pinhole fleck
[6 empty] | Piping | Straight Run | Fiberglass | NS
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2015 |  | Y |  |  | Floor |  | Clay | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling |  | Wood | NS | [6 empty] | VS004 | 2' x 4' pinhole fleck
[6 empty] | Piping | Straight Run | Fiberglass | NS
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2007, 2007C, 2007D | 2007 | Y | Male Changeroom | 012 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | Y | A | N | Sf | 120 | - | - | S008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2006, 2006A, 2006B | 2006 | Y | Female Change | 013 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | Y | A | N | SF | 200 | - | - | S009 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 1006 | 1006 | Y |  |  | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2020, 2020A | 2020 | Y | Office | 029 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S014 was collected but not confirmed ACM. S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3C04, 3C03 | 3024 | Y | Diving Board | 038 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2013, 2013A | 2013 | Y | Office | 042 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2026 | 2026 | Y |  |  | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3000 | 3000 | Y |  |  | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping |  | Plastic | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Mechanical |  | Not Insulated
[6 empty] | Other | N/F
AQ | 3E01 |  | Y |  |  | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2S03 |  | Y |  |  | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3C05 |  | Y |  |  | Floor |  | Rubber | NS | [14 empty] | PLEL | NS as is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Fiberglass | NS | [15 empty] | NS as is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 3C06 |  | Y |  |  | Floor |  | Rubber | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Ceiling | Acoustic tile | Fiberglass | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AQ | 2005 | 2005 | Y | Storage |  | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 45 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F