## BusAdmin
Room # | Room # (numeric) | Room Accessed (Y/N) | Location Description | PLEL Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[11 empty] | Unit of Measure | Condition
[12 empty] | Good | Fair | Poor
1000 | 1000 | Y | Storage Room |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as the material is not suspect ACM
1000 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 111 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1000 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1000 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck
1000 |  |  |  |  | Piping | N/F
1000 |  |  |  |  | Mechanical | Steel | [17 empty] | NS as the material is not suspect ACM
1000 |  |  |  |  | Other | N/F
1001 | 1001 | Y | Office | 002 | Floor | Tile | Vinyl tile | N | [6 empty] | S001 | 12' x 12' White | [6 empty] | PLEL
1001 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S001 | 12' x 12' White
1001 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1001 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 20 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1001 |  |  |  |  | Piping | N/F
1001 |  |  |  |  | Mechanical | N/F
1001 |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
1001A | 1001 | Y | Office | 001 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1001A |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1001A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1001A |  |  |  |  | Piping | N/F
1001A |  |  |  |  | Mechanical | N/F
1001A |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
1003 | 1003 | Y | Office | 166 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
1003 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1003 |  |  |  |  | Ceiling | Panel | Steel | NS | [15 empty] | NS as wood fibre is not suspect ACM>
1003 |  |  |  |  | Piping | N/F
1003 |  |  |  |  | Mechanical | N/F
1003 |  |  |  |  | Other | Structure | Spray insulation | N | [6 empty] | S049 | Spray insulation
1003A | 1003 | Y | Office | 166 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
1003A |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1003A |  |  |  |  | Ceiling | Panel | Steel | NS | [15 empty] | NS as wood fibre is not suspect ACM
1003A |  |  |  |  | Piping | N/F
1003A |  |  |  |  | Mechanical | N/F
1003A |  |  |  |  | Other | Structure | Spray insulation | N | [6 empty] | S049 | Spray insulation
1004 | 1004 | Y |  |  | Floor | Tile | Vinyl tile | NS | [6 empty] | VS002 | 12' x 12' white/ grey | [6 empty] | PLEL
1004 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 |  |  | S025 was collected but not confirmed ACM. S007 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
1004 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 4' pinhole fissure
1004 |  |  |  |  | Piping | N/F
1004 |  |  |  |  | Mechanical | N/F
1004 |  |  |  |  | Other | N/F | [17 empty] | No acces above the ceiling.
1005 | 1005 | Y | Office | 003 | Floor | Sheet Flooring | VSF | N | [6 empty] | S002 | Grey with large white and black streaks | [6 empty] | PLEL
1005 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S002 | Grey with large white and black streaks
1005 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S003 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1005 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S004 | 2' x 4' hole and fleck
1005 |  |  |  |  | Piping | Elbows/Fittings | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
1005 |  |  |  |  | Mechanical | N/F
1005 |  |  |  |  | Other | Acoustic tile | Lay-in T-bar | N | [6 empty] | S005 | 2' x 4' pinhole and fleck
1006 | 1006 | Y | Office | 004 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and black streaks | [6 empty] | PLEL | NS as the material was visually similar to S002.
1006 |  |  |  |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and black streaks | [7 empty] | NS as the material was visually similar to S002.
1006 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1006 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S006 | 2' x 4' longitudinal fissure and pinhole
1006 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually similar to S005.
1006 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' hole and fleck | [7 empty] | NS as the material was visually similar to S004.
1006 |  |  |  |  | Piping | N/F
1006 |  |  |  |  | Mechanical | N/F
1006 |  |  |  |  | Other | N/F
1007 | 1007 | Y | Office | 005 | Floor | Tile | Vinyl tile | N | [6 empty] | S007 | 12' x 12' Light blue with abundant blue and white fleck | [6 empty] | PLEL
1007 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S007 | 12' x 12' Light blue with abundant blue and white fleck
1007 |  |  |  |  | Floor | Tile | Vinyl tile | N | [6 empty] | S008 | 12' x 12' Light grey with grey and white flecks
1007 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S008 | 12' x 12' Light grey with grey and white flecks
1007 |  |  |  |  | Floor | Tile | Vinyl tile | N | [6 empty] | S009 | 12' x 12' Blue with abundant dark blue and white flecks
1007 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S009 | 12' x 12' Blue with abundant dark blue and white flecks
1007 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 520 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1007 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' hole and fleck | [7 empty] | NS as the material was visually similar to S004.
1007 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually similar to S005.
1007 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 4' longitudinal fissure and pinhole | [7 empty] | NS as the material was visually similar to S006.
1007 |  |  |  |  | Piping | N/F
1007 |  |  |  |  | Mechanical | N/F
1007 |  |  |  |  | Other | N/f
1007A | 1007 | Y | Office | 005 | Floor | Tile | Vinyl tile | N | [6 empty] | S007 | 12' x 12' Light blue with abundant blue and white fleck | [6 empty] | PLEL
1007A |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S007 | 12' x 12' Light blue with abundant blue and white fleck
1007A |  |  |  |  | Floor | Tile | Vinyl tile | N | [6 empty] | S008 | 12' x 12' Light grey with grey and white flecks
1007A |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S008 | 12' x 12' Light grey with grey and white flecks
1007A |  |  |  |  | Floor | Tile | Vinyl tile | N | [6 empty] | S009 | 12' x 12' Blue with abundant dark blue and white flecks
1007A |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S009 | 12' x 12' Blue with abundant dark blue and white flecks
1007A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 520 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1007A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' hole and fleck | [7 empty] | NS as the material was visually similar to S004.
1007A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually similar to S005.
1007A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 4' longitudinal fissure and pinhole | [7 empty] | NS as the material was visually similar to S006.
1007A |  |  |  |  | Piping | N/F
1007A |  |  |  |  | Mechanical | N/F
1007A |  |  |  |  | Other | N/f
1007B | 1007 | Y | Custodial Room |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as the material is not suspect ACM
1007B |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as the material is not suspect ACM
1007B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck
1007B |  |  |  |  | Piping | N/F
1007B |  |  |  |  | Mechanical | N/F
1007B |  |  |  |  | Other |  | Caulking | N | [6 empty] | S012 | Window caulking
1008 | 1008 | Y | Office |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS010 | Light grey with white and dark grey streaks | [6 empty] | PLEL
1008 |  |  |  |  | Wall | Concrete | Concrete
1008 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S004.
1008 |  |  |  |  | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as the material is not suspect ACM
1008 |  |  |  |  | Mechanical | N/F
1008 |  |  |  |  | Other | Ductwork | Steel | N | [15 empty] | NS as the material is not suspect ACM
1009 | 1009 | Y | Office | 006 | Floor | Sheet Flooring | VSF | N | [6 empty] | S010 | Light grey with white and dark grey streaks | [6 empty] | PLEL
1009 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S010 | Light grey with white and dark grey streaks
1009 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S011 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1009 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S013 | 2' x 2' pinhole fleck
1009 |  |  |  |  | Piping | N/F
1009 |  |  |  |  | Mechanical | N/F
1009 |  |  |  |  | Other | Window | Caulking | N | [6 empty] | S012 | Window caulking
1010 | 1010 | Y | Office |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS010 | Light grey with white and dark grey streaks | [6 empty] | PLEL
1010 |  |  |  |  | Wall | Concrete | Concrete | [16 empty] | NS as the material is not suspect ACM
1010 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S004.
1010 |  |  |  |  | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as the material is not suspect ACM
1010 |  |  |  |  | Mechanical | N/F
1010 |  |  |  |  | Other | Ductwork | Steel | N | [15 empty] | NS as the material is not suspect ACM
1011 | 1011 | Y | Office | 007 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002.
1011 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002.
1011 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 768 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1011 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
1011 |  |  |  |  | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
1011 |  |  |  |  | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
1011 |  |  |  |  | Other | N/F
1011A | 1011A | Y | Storage Room | 007 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as the material is not suspect ACM
1011A |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as the material is not suspect ACM
1011A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 75 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1011A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck
1011A |  |  |  |  | Piping | Straight Run | Tar mastic | N | [6 empty] | S024 | Tar mastic on ductwork | [7 empty] | Comfirmend Non ACM
1011A |  |  |  |  | Poping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
1011A |  |  |  |  | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
1012 | 1012 | Y | Office | 010 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1012 |  |  |  |  | Wall | Drywall | DWJC | Y | A | N | SF | 2000 | - | - | S015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
1012 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS006 | 2' x 4' longitudinal fissure and pinhole | [7 empty] | NS as the material was visually similar to S006.
1012 |  |  |  |  | Piping | N/F
1012 |  |  |  |  | Mechanical | N/F
1012 |  |  |  |  | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually the same as S005.
1012A | 1012 | Y | Office | 010 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1012A |  |  |  |  | Wall | Drywall | DWJC | Y | A | N | SF | 2000 | - | - | S015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
1012A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS006 | 2' x 4' longitudinal fissure and pinhole | [7 empty] | NS as the material was visually similar to S006.
1012A |  |  |  |  | Piping | N/F
1012A |  |  |  |  | Mechanical | N/F
1012A |  |  |  |  | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually the same as S005.
1012B | 1012 | Y | Office | 010 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1012B |  |  |  |  | Wall | Drywall | DWJC | Y | A | N | SF | 2000 | - | - | S015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
1012B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS006 | 2' x 4' longitudinal fissure and pinhole | [7 empty] | NS as the material was visually similar to S006.
1012B |  |  |  |  | Piping | N/F
1012B |  |  |  |  | Mechanical | N/F
1012B |  |  |  |  | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually the same as S005.
1012C | 1012 | Y | Office | 009 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1012C |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1012C |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF |  |  |  | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1012C |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | Y | D | N | EA | 5 | - | - | S014 | Tar mastic on FG pipe insulation | 10 | 0 | 0 | 0 | 0 | 0
1012C |  |  |  |  | Mechanical | Ductwork | Fiberglass | NS
1012C |  |  |  |  | Other | N/F
1012D | 1012 | Y | Office | 008 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1012D |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1012D |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 70 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1012D |  |  |  |  | Piping | N/F
1012D |  |  |  |  | Mechanical | N/F
1012D |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
1013 | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013 |  |  |  |  | Mechanical | N/F
1013 |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013A | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013A |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013A |  |  |  |  | Mechanical | N/F
1013A |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013B | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013B |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013B |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013B |  |  |  |  | Mechanical | N/F
1013B |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013C | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013C |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013C |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013C |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013C |  |  |  |  | Mechanical | N/F
1013C |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013D | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013D |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013D |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013D |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013D |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013D |  |  |  |  | Mechanical | N/F
1013D |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013E | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013E |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013E |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013E |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013E |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013E |  |  |  |  | Mechanical | N/F
1013E |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013F | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013F |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013F |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013F |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013F |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013F |  |  |  |  | Mechanical | N/F
1013F |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013G | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013G |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013G |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013G |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013G |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013G |  |  |  |  | Mechanical | N/F
1013G |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1013H | 1013 | Y | Office | 138 | Floor | Tile | Vinyl tile | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks | [6 empty] | PLEL
1013H |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S047 | 12' x 12' Light brown with abundant white and brown flecks
1013H |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1512 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1013H |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
1013H |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1013H |  |  |  |  | Mechanical | N/F
1013H |  |  |  |  | Other | Elbows/Fittings | Parging cement | N | [6 empty] | S048 | Parging cement
1015 | 1015 | Y | Office | 022 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S005.
1015 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2'x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
1015 |  |  |  |  | Piping | N/F
1015 |  |  |  |  | Mechanical | N/F
1015 |  |  |  |  | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' hole and fleck | [7 empty] | NS as the material was visually similar to S004.
1015A | 1015 | Y | Server Room | 167 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S019.
1015A |  |  |  |  | Piping | N/F
1015A |  |  |  |  | Mechanical | N/F
1015A |  |  |  |  | Other | N/F
1015B | 1015 | Y | Office | 012 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually the same as S005.
1015B |  |  |  |  | Piping | N/F
1015B |  |  |  |  | Mechanical | N/F
1015B |  |  |  |  | Other | N/F
1015 C | 1015 | Y | Office | 013 | Floor | Sheet Flooring | VSF | N | [6 empty] | S017 | Light grey speckled | [6 empty] | PLEL
1015 C |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S017 | Light grey speckled
1015 C |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 59 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S005.
1015 C |  |  |  |  | Piping | N/F
1015 C |  |  |  |  | Mechanical | N/f
1015 C |  |  |  |  | Other | N/F
1015D | 1015 | Y | Office | 014 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015D |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 244 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015D |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
1015D |  |  |  |  | Piping | N/F
1015D |  |  |  |  | Mechanical | N/F
1015D |  |  |  |  | Other | N/F
1015E | 1015 | Y | Office | 014 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015E |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 244 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015E |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
1015E |  |  |  |  | Piping | N/F
1015E |  |  |  |  | Mechanical | N/F
1015E |  |  |  |  | Other | N/F
1015 F | 1015 | Y | Office | 015 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 F |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 244 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 F |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
1015 F |  |  |  |  | Piping | N/F
1015 F |  |  |  |  | Mechanical | N/F
1015 F |  |  |  |  | Other
1015 G | 1015 | Y | Office | 016 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 G |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 244 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 G |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
1015 G |  |  |  |  | Piping | N/F
1015 G |  |  |  |  | Mechanical | N/F
1015 G |  |  |  |  | Other
1015 H | 1015 | Y | Office | 017 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 H |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 244 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 H |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
1015 H |  |  |  |  | Piping | N/F
1015 H |  |  |  |  | Mechanical | N/F
1015 H |  |  |  |  | Other
1015 J | 1015 | Y | Office | 018 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 J |  |  |  |  | Wall | Drywall | DWJC | Y | A | N | SF | 100 | - | - | S018 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
1015 J |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S019 | 2' x 4' pinhole and small fissure
1015 J |  |  |  |  | Piping | N/F
1015 J |  |  |  |  | Mechanical | N/F
1015 J |  |  |  |  | Other
1015 K | 1015 | Y | Office | 019 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 K |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 K |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S013
1015 K |  |  |  |  | Piping | N/F
1015 K |  |  |  |  | Mechanical | N/F
1015 K |  |  |  |  | Other
1015 L | 1015 | Y | Office | 020 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 L |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 L |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S013
1015 L |  |  |  |  | Piping | N/F
1015 L |  |  |  |  | Mechanical | N/F
1015 L |  |  |  |  | Other
1015 M | 1015 | Y | Office | 021 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1015 M |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1015 M |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S005.
1015 M |  |  |  |  | Piping | N/F
1015 M |  |  |  |  | Mechanical | N/F
1015 M |  |  |  |  | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' hole and fleck | [7 empty] | NS as the material was visually similar to S004.
1017 | 1017 | Y | Atrium | 023 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1017 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1017 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 2200 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1017 |  |  |  |  | Piping | N/F
1017 |  |  |  |  | Mechanical | N/F
1017 |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
1C01 |  | Y | Hallway | 024 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1C01 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1C01 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' hole and fleck | [7 empty] | NS as the material was visually the same as S004.
1C01 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
1C01 |  |  |  |  | Mechanical | N/F
1C01 |  |  |  |  | Other | N/F | [17 empty] | Limited access above ceiling
1C02 |  | Y | Hallway | 025 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1C02 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1C02 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole and fleck | [7 empty] | NS as the material was visually the same as S005.
1C02 |  |  |  |  | Piping | N/F
1C02 |  |  |  |  | Mechanical | N/F
1C02 |  |  |  |  | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' hole and fleck | [7 empty] | NS as the material was visually similar to S004.
1V01 |  | Y | Corridor | 026 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1V01 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1V01 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 180 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1V01 |  |  |  |  | Piping | N/F
1V01 |  |  |  |  | Mechanical | N/F
1V01 |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
1V02 |  | Y | Corridor | 026 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1V02 |  |  |  |  | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1V02 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 180 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1V02 |  |  |  |  | Piping | N/F
1V02 |  |  |  |  | Mechanical | N/F
1V02 |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
1V04 |  | Y | Office | 011 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
1V04 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1V04 |  |  |  |  | Ceiling | Drywall | DWJC | Y | A | N | SF | 200 | - | - | S016 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
1V04 |  |  |  |  | Piping | N/F
1V04 |  |  |  |  | Mechanical | N/F
1V04 |  |  |  |  | Other | N/f | [17 empty] | No access above ceiling.
1S01 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1S01 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S01 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S01 |  |  |  |  | Piping | N/F
1S01 |  |  |  |  | Mechanical | N/F
1S01 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
1S02 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1S02 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S02 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S02 |  |  |  |  | Piping | N/F
1S02 |  |  |  |  | Mechanical | N/F
1S02 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
1V03 |  | Y | Corridor | 026 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1V03 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
1V03 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 180 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1V03 |  |  |  |  | Piping | N/F
1V03 |  |  |  |  | Mechanical | N/F
1V03 |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
1S03 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1S03 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S03 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S03 |  |  |  |  | Piping | N/F
1S03 |  |  |  |  | Mechanical | N/F
1S03 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
1S04 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
1S04 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S04 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
1S04 |  |  |  |  | Piping | N/F
1S04 |  |  |  |  | Mechanical | N/F
1S04 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
1E01 | 1E01,2E01, 3E01 | Y | Elevator | 165 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS041 | 12' x 12' White with brown flecks | [6 empty] | PLEL | NS as the material was visually similar to S041.
1E01 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS041 | 12' x 12' White with brown flecks | [7 empty] | NS as the material was visually similar to S041
1E01 |  |  |  |  | Wall |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
1E01 |  |  |  |  | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
1E01 |  |  |  |  | Piping | N/F
1E01 |  |  |  |  | Mechanical | N/F
1E01 |  |  |  |  | Other | N/f
2000 | 2000 | Y | Office | 121 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2000 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2000 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2000 |  |  |  |  | Piping | N/f
2000 |  |  |  |  | Mechanical | N/F
2000 |  |  |  |  | Other | N/F
2001 | 2001 | Y | Office | 121 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2001 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2001 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2001 |  |  |  |  | Piping | N/f
2001 |  |  |  |  | Mechanical | N/F
2001 |  |  |  |  | Other | N/F
2002 | 2002 | Y | Janitorial Room |  | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2002 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
2002 |  |  |  |  | Ceiling | Steel | Steel | NS | [15 empty] | NS as the material is not suspect ACM
2002 |  |  |  |  | Piping | N/f
2002 |  |  |  |  | Mechanical | N/F
2002 |  |  |  |  | Other | N/F
2002A | 2002 | Y | Office | 034 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2002A |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
2002A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2002A |  |  |  |  | Piping | N/F
2002A |  |  |  |  | Mechanical | N/F
2002A |  |  |  |  | Other | N/F
2003 | 2003 | Y | Office | 032 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2003 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 130 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2003 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2003 |  |  |  |  | Piping | N/F
2003 |  |  |  |  | Mechanical | N/F
2003 |  |  |  |  | Other | N/F
2004 | 2004 | Y | Office | 031 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2004 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 130 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2004 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2004 |  |  |  |  | Piping | N/F
2004 |  |  |  |  | Mechanical | N/F
2004 |  |  |  |  | Other | N/F
2005 | 2005 | Y | Office | 029 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2005 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 130 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2005 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2005 |  |  |  |  | Piping | N/F
2005 |  |  |  |  | Mechanical | N/F
2005 |  |  |  |  | Other | N/F
2006 | 2006 | Y | Office | 030 or 033 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2006 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 130 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2006 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2006 |  |  |  |  | Piping | N/F
2006 |  |  |  |  | Mechanical | N/F
2006 |  |  |  |  | Other | N/F
2007 | 2007 | Y | Office | 114 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2007 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2007 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2007 |  |  |  |  | Piping | N/f
2007 |  |  |  |  | Mechanical | N/F
2007 |  |  |  |  | Other | N/F
2008 | 2008 | Y | Office | 113 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2008 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2008 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2008 |  |  |  |  | Piping | N/f
2008 |  |  |  |  | Mechanical | N/F
2008 |  |  |  |  | Other | N/F
2009 | 2009 | Y | Office | 112 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2009 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2009 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2009 |  |  |  |  | Piping | N/f
2009 |  |  |  |  | Mechanical | N/F
2009 |  |  |  |  | Other | N/F
2010 | 2010 | Y | Office | 111 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS041 | 12' x 12' White with brown flecks | [6 empty] | PLEL | NS as the material was visually similar to S041
2010 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS041 | 12' x 12' White with brown flecks | [7 empty] | NS as the material was visually similar to S041
2010 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2010 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2010 |  |  |  |  | Piping | N/f
2010 |  |  |  |  | Mechanical | N/F
2010 |  |  |  |  | Other | N/F
2011 | 2011 | Y | Office | 110 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2011 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2011 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2011 |  |  |  |  | Piping | N/F
2011 |  |  |  |  | Mechanical | N/F
2011 |  |  |  |  | Other | N/F
2012 | 2012 | Y | Office | 116 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2012 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2012 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2012 |  |  |  |  | Piping | N/f
2012 |  |  |  |  | Mechanical | N/F
2012 |  |  |  |  | Other | N/F
2013 | 2013 | Y | Office | 117 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2013 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2013 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2013 |  |  |  |  | Piping | N/f
2013 |  |  |  |  | Mechanical | N/F
2013 |  |  |  |  | Other | N/F
2014 | 2014 | Y | Office | 028 | Floor | Tile | Vinyl tile | Y | A | N | SF | 408 | - | - | S020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | Tile only, no mastic analyzed/
2014 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 408 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2014 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2014 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2014 |  |  |  |  | Mechanical | N/F
2014 |  |  |  |  | Other | N/f
2015 | 2015 | Y | Office | 027 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS010 | Light grey with white and dark grey streaks | [6 empty] | PLEL | NS as the material was visually similar to S010
2015 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS010 | Light grey with white and dark grey streaks | [7 empty] | NS as the material was visually similar to S010
2015 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2015 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S013
2015 |  |  |  |  | Piping | N/F
2015 |  |  |  |  | Mechanical | N/F
2015 |  |  |  |  | Other | Window | Caulking | NS | [6 empty] | VS012 | Window caulking | [7 empty] | NS as the material was visually similar to S012
2016 | 2016 | Y | Office | 118 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2016 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2016 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2016 |  |  |  |  | Piping | N/f
2016 |  |  |  |  | Mechanical | N/F
2016 |  |  |  |  | Other | N/F
2017 | 2017 | Y | Office | 119 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2017 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2017 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019.
2017 |  |  |  |  | Piping | N/f
2017 |  |  |  |  | Mechanical | N/f
2017 |  |  |  |  | Other | N/F
2018 | 2018 | Y | Office | 120 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2018 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2018 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2018 |  |  |  |  | Piping | N/f
2018 |  |  |  |  | Mechanical | N/F
2018 |  |  |  |  | Other | N/F
2019 | 2019 | Y | Office | 122 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2019 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2019 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2019 |  |  |  |  | Piping | N/f
2019 |  |  |  |  | Mechanical | N/F
2019 |  |  |  |  | Other | N/F
2020 | 2020 | Y | Office | 123 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2020 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2020 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2020 |  |  |  |  | Piping | N/f
2020 |  |  |  |  | Mechanical | N/F
2020 |  |  |  |  | Other | N/F
2021 | 2021 | Y | Office | 124 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2021 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2021 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2021 |  |  |  |  | Piping | N/f
2021 |  |  |  |  | Mechanical | N/F
2021 |  |  |  |  | Other | N/F
2022 | 2022 | Y | Office |  | Wall | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
2022 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2022 |  |  |  |  | Ceiling | Steel | Steel | NS
2022 |  |  |  |  | Piping | N/f
2022 |  |  |  |  | Mechanical | N/F
2022 |  |  |  |  | Other | N/F
2023 | 2023 | Y | Office | 125 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2023 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2023 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2023 |  |  |  |  | Piping | N/f
2023 |  |  |  |  | Mechanical | N/F
2023 |  |  |  |  | Other | N/F
2024 | 2024 | Y | Office | 126 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2024 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2024 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2024 |  |  |  |  | Piping | N/f
2024 |  |  |  |  | Mechanical | N/F
2024 |  |  |  |  | Other | N/F
2025 | 2025 | Y | Office | 127 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
2025 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2025 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2025 |  |  |  |  | Piping | N/f
2025 |  |  |  |  | Mechanical | N/F
2025 |  |  |  |  | Other | N/F
2026 | 2026 | Y | Storage Room |  | Wall | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
2026 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 190 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | Confirmed ACM - S015
2026 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' pinhole and fissure
2026 |  |  |  |  | Piping | N/f
2026 |  |  |  |  | Mechanical | N/F
2026 |  |  |  |  | Other | Ductwork | Non insulated | NS | [15 empty] | NS as the material is not suspect ACM
2026A | 2026 | Y | Office | 036 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2026A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S021 was collected but not confirmed ACM.S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2026A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2026A |  |  |  |  | Piping | N/F
2026A |  |  |  |  | Mechanical | N/F
2026A |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
2026B | 2026 | Y | Office | 037 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2026B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2026B |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2026B |  |  |  |  | Piping | N/F
2026B |  |  |  |  | Mechanical | N/F
2026B |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
2027 | 2027 | Y | Office | 038 | Floor | Tile | Vinyl tile | N | [6 empty] | S022 | 12' x 12' Pink | [6 empty] | PLEL
2027 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S022 | 12' x 12' Pink
2027 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027 |  |  |  |  | Mechanical | N/F
2027 |  |  |  |  | Other | N/F
2027A | 2027A | Y | Office | 038 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL
2027A |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink
2027A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027A |  |  |  |  | Mechanical | N/F
2027A |  |  |  |  | Other | N/F
2027B | 2027B | Y | Office | 038 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL
2027B |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink
2027B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027B |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027B |  |  |  |  | Mechanical | N/F
2027B |  |  |  |  | Other | N/F
2027C | 2027C | Y | Office | 038 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL
2027C |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink
2027C |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027C |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027C |  |  |  |  | Mechanical | N/F
2027C |  |  |  |  | Other | N/F
2027D | 2027D | Y | Office | 038 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL
2027D |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink
2027D |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027D |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027D |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027D |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027D |  |  |  |  | Mechanical | N/F
2027D |  |  |  |  | Other | N/F
2027E | 2027E | Y | Office | 038 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL
2027E |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink
2027E |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027E |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027E |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027E |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027E |  |  |  |  | Mechanical | N/F
2027E |  |  |  |  | Other | N/F
2027F | 2027F | Y | Office | 038 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL
2027F |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink
2027F |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027F |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027F |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027F |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027F |  |  |  |  | Mechanical | N/F
2027F |  |  |  |  | Other | N/F
2027G | 2027G | Y | Office | 038 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL
2027G |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink
2027G |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S023 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2027G |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
2027G |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2027G |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
2027G |  |  |  |  | Mechanical | N/F
2027G |  |  |  |  | Other | N/F
2028 | 2028 | Y | Office | 128 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2028 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2028 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2028 |  |  |  |  | Piping | N/f
2028 |  |  |  |  | Mechanical | N/F
2028 |  |  |  |  | Other | N/F
2028A | 2028 | Y | Office | 039 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2028A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 190 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2028A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' pinhole and fissure | [7 empty] | NS as the material was visually similar to S004.
2028A |  |  |  |  | Piping | N/F
2028A |  |  |  |  | Mechanical | N/F
2028A |  |  |  |  | Other | N/F
2028B | 2028 | Y | Office | 040 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2028B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 190 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2028B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' pinhole and fissure | [7 empty] | NS as the material was visually similar to S004.
2028B |  |  |  |  | Piping | N/F
2028B |  |  |  |  | Mechanical | N/F
2028B |  |  |  |  | Other | N/F
2029 | 2029 | Y | Office | 041 | Floor | Tile | Vinyl tile | N | [6 empty] | S026 | 12' x 12' White with brown streak | [6 empty] | PLEL
2029 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S026 | 12' x 12' White with brown streak
2029 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1370 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM; 1370 must be the total of the 4 rooms.
2029 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 4' pinhole and longitudinal fissure | [7 empty] | NS as the material was visually similar to S006.
2029 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2029 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S025 | 2' x 4' pinhole fleck
2029 |  |  |  |  | Piping | N/F
2029 |  |  |  |  | Mechanical | Ductwork | Tar mastic | N | [6 empty] | S024 | Tar mastic on ductwork (seams)
2029 |  |  |  |  | Other | N/f
2029A | 2029A | Y | Office | 041 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS026 | 12' x 12' White with brown streak | [6 empty] | PLEL
2029A |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS026 | 12' x 12' White with brown streak
2029A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1370 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2029A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 4' pinhole and longitudinal fissure | [7 empty] | NS as the material was visually similar to S006.
2029A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2029A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S025 | 2' x 4' pinhole fleck
2029A |  |  |  |  | Piping | N/F
2029A |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork
2029A |  |  |  |  | Other | N/f
2029C | 2029C | Y | Office | 041 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS026 | 12' x 12' White with brown streak | [6 empty] | PLEL
2029C |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS026 | 12' x 12' White with brown streak
2029C |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1370 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2029C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 4' pinhole and longitudinal fissure | [7 empty] | NS as the material was visually similar to S006.
2029C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2029C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S025 | 2' x 4' pinhole fleck
2029C |  |  |  |  | Piping | N/F
2029C |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork
2029C |  |  |  |  | Other | N/f
2030 | 2030 | Y | Office | 041 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS026 | 12' x 12' White with brown streak | [6 empty] | PLEL
2030 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS026 | 12' x 12' White with brown streak
2030 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1370 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2030 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 4' pinhole and longitudinal fissure | [7 empty] | NS as the material was visually similar to S006.
2030 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2030 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S025 | 2' x 4' pinhole fleck
2030 |  |  |  |  | Piping | N/F
2030 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork
2030 |  |  |  |  | Other | N/f
2031 | 2031 | Y | Office | 035 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2031 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
2031 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2031 |  |  |  |  | Piping | N/F
2031 |  |  |  |  | Mechanical | N/F
2031 |  |  |  |  | Other | N/F
2031A | 2031 | Y | Office | 035 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2031A |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
2031A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 80 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2031A |  |  |  |  | Piping | N/F
2031A |  |  |  |  | Mechanical | N/F
2031A |  |  |  |  | Other | N/F
2032 | 2032 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2032 |  |  |  |  | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
2032 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 2200 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2032 |  |  |  |  | Piping | N/F
2032 |  |  |  |  | Mechanical | N/F
2032 |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
2033 | 2033 | Y | Office | 042 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2033 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 140 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2033 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S005.
2033 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2033 |  |  |  |  | Piping | N/F
2033 |  |  |  |  | Mechanical | N/F
2033 |  |  |  |  | Other | N/F
2034 | 2034 | Y | Office | 043 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
2034 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 140 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2034 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S005.
2034 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S019.
2034 |  |  |  |  | Piping | N/F
2034 |  |  |  |  | Mechanical | N/F
2034 |  |  |  |  | Other | N/F
2035 | 2035 | Y | Office |  | Floor |  | Carpet | [15 empty] | PLEL | NS as carpet is not suspect ACM.
2035 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 450 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | Confirmed ACM S015
2035 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 4' pinhole and fissure
2035 |  |  |  |  | Piping | N/F
2035 |  |  |  |  | Mechanical | N/F
2035 |  |  |  |  | Other | N/F
2036 | 2036 | Y | Office | 137 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2036 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2036 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2036 |  |  |  |  | Piping | N/f
2036 |  |  |  |  | Mechanical | N/F
2036 |  |  |  |  | Other | N/F
2037 | 2037 | Y | Office | 136 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2037 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2037 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2037 |  |  |  |  | Piping | N/f
2037 |  |  |  |  | Mechanical | N/F
2037 |  |  |  |  | Other | N/F
2038 | 2038 | Y | Office | 135 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2038 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2038 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2038 |  |  |  |  | Piping | N/f
2038 |  |  |  |  | Mechanical | N/F
2038 |  |  |  |  | Other | N/F
2039 | 2039 | Y | Office | 134 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2039 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2039 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2039 |  |  |  |  | Piping | N/f
2039 |  |  |  |  | Mechanical | N/F
2039 |  |  |  |  | Other | N/F
2040 | 2040 | Y | Office | 133 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2040 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2040 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2040 |  |  |  |  | Piping | N/f
2040 |  |  |  |  | Mechanical | N/F
2040 |  |  |  |  | Other | N/F
2041 | 2041 | Y | Office |  | Wall | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
2041 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | Confirmed ACM - S015
2041 |  |  |  |  | Ceiling | Steel | Steel | NS
2041 |  |  |  |  | Piping | N/f
2041 |  |  |  |  | Mechanical | N/F
2041 |  |  |  |  | Other | N/F
2042 | 2042 | Y | Office | 132 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2042 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2042 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2042 |  |  |  |  | Piping | N/f
2042 |  |  |  |  | Mechanical | N/F
2042 |  |  |  |  | Other | N/F
2043 | 2043 | Y | Office | 131 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2043 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2043 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2043 |  |  |  |  | Piping | N/f
2043 |  |  |  |  | Mechanical | N/F
2043 |  |  |  |  | Other | N/F
2044 | 2044 | Y | Office | 130 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2044 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2044 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2044 |  |  |  |  | Piping | N/f
2044 |  |  |  |  | Mechanical | N/F
2044 |  |  |  |  | Other | N/F
2045 | 2045 | Y | Office | 129 | Floor | Tile | Vinyl tile | P | A | N | SF | 120 | - | - | VS020 | 12' x 12' White with large brown streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S020. No mastic analyzed.
2045 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2045 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
2045 |  |  |  |  | Piping | N/f
2045 |  |  |  |  | Mechanical | N/F
2045 |  |  |  |  | Other | N/F
2C01 |  | Y | Hallway | 044 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS010 | Light grey with White and dark grey streaks | [6 empty] | PLEL | NS as the material was visually similar to S010.
2C01 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS010 | Light grey with white and dark grey streaks | [7 empty] | NS as the material was visually similar to S010
2C01 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1370 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S027 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2C01 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually the same as S019
2C01 |  |  |  |  | Piping | N/F
2C01 |  |  |  |  | Mechanical | N/F
2C01 |  |  |  |  | Other | N/F
2C02 |  | Y | Hallway | 045 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS010 | Light grey with White and dark grey streaks | [6 empty] | PLEL | NS as the material was visually similar to S010.
2C02 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS010 | Light grey with white and dark grey streaks | [7 empty] | NS as the material was visually similar to S010
2C02 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1370 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2C02 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually the same as S019
2C02 |  |  |  |  | Piping | N/F
2C02 |  |  |  |  | Mechanical | N/F
2C02 |  |  |  |  | Other | N/F
2C03 |  | Y | Hallway | 045 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS010 | Light grey with White and dark grey streaks | [6 empty] | PLEL | NS as the material was visually similar to S010.
2C03 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS010 | Light grey with white and dark grey streaks | [7 empty] | NS as the material was visually similar to S010
2C03 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1370 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2C03 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole and small fissure | [7 empty] | NS as the material was visually the same as S019
2C03 |  |  |  |  | Piping | N/F
2C03 |  |  |  |  | Mechanical | N/F
2C03 |  |  |  |  | Other | N/F
2S01 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2S01 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S01 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S01 |  |  |  |  | Piping | N/F
2S01 |  |  |  |  | Mechanical | N/F
2S01 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
2S02 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2S02 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S02 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S02 |  |  |  |  | Piping | N/F
2S02 |  |  |  |  | Mechanical | N/F
2S02 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
2S03 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2S03 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S03 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S03 |  |  |  |  | Piping | N/F
2S03 |  |  |  |  | Mechanical | N/F
2S03 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
2S04 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
2S04 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S04 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
2S04 |  |  |  |  | Piping | N/F
2S04 |  |  |  |  | Mechanical | N/F
2S04 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
3000 | 3000 | Y | Office |  | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
3000 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3000 |  |  |  |  | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
3000 |  |  |  |  | Piping | N/F
3000 |  |  |  |  | Mechanical | N/F
3000 |  |  |  |  | Other | N/F
3000A | 3000 | Y | Office | 049 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
3000A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3000A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3000A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3000A |  |  |  |  | Mechanical | N/F
3000A |  |  |  |  | Other | N/F | [17 empty] | Limited access above ceiling
3000B | 3000 | Y | Office | 050 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
3000B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3000B |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3000B |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3000B |  |  |  |  | Mechanical | N/F
3000B |  |  |  |  | Other | N/F | [17 empty] | Limited access above ceiling
3001 |  | Y | Janitor Closet | 046 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
3001 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
3001 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S029 was collected but not confirmed ACM.S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3001 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3001 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S028 | 2' x 2' pinhole and small fissure
3001 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 25 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3001 |  |  |  |  | Mechanical | N/F
3001 |  |  |  |  | Other | N/F
3002 | 3002 | Y | Office | 107 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3002 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1000 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3002 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S013.
3002 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | Ea | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3002 |  |  |  |  | Mechanical | N/F
3002 |  |  |  |  | Other | N/F
3003 | 3003 | Y | Office | 108 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS038 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S038.
3003 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS038 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S038.
3003 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3003 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3003 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3003 |  |  |  |  | Mechanical | N/F
3003 |  |  |  |  | Other | N/F
3004 | 3004 | Y | Office | 109 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS038 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S038.
3004 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS038 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S038.
3004 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3004 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3004 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3004 |  |  |  |  | Mechanical | N/F
3004 |  |  |  |  | Other | N/F
3005 | 3005 | Y | Office | 168 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
3005 |  |  |  |  | Wall | Drywall | DWJC | p | A | N | SF | 60 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3005 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
3005 |  |  |  |  | Piping | Straight Run/Elbows | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
3005 |  |  |  |  | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
3005 |  |  |  |  | Other | N/F
3006 | 3006 | Y | Storage |  | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3006 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 180 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3006 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' pinhole fleck
3006 |  |  |  |  | Piping | N/F
3006 |  |  |  |  | Mechanical | Ductwork | Non insulated | NS
3006 |  |  |  |  | Other | N/F
3007 | 3007 | Y | Office | 106 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3007 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1000 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3007 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S046 | 2' x 2' solid wave
3007 |  |  |  |  | Piping | N/F
3007 |  |  |  |  | Mechanical | N/F
3007 |  |  |  |  | Other | N/F
3007A | 3007A | Y | Storage |  | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
3007A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 750 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3007A |  |  |  |  | Ceiling | N/F
3007A |  |  |  |  | Piping | Straight Run/Elbows | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
3007A |  |  |  |  | Mechanical | N/F |  | NS
3007A |  |  |  |  | Other | N/F
3008 | 3008 | Y | Office | 163 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
3008 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
3008 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 640 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3008 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
3008 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S028
3008 |  |  |  |  | Piping | N/F
3008 |  |  |  |  | Mechanical | N/F
3008 |  |  |  |  | Other | N/F
3009 | 3009 | Y | Office | 047 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
3009 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
3009 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 640 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S030 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3009 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS005 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S005.
3009 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S028
3009 |  |  |  |  | Piping | N/F
3009 |  |  |  |  | Mechanical | N/F
3009 |  |  |  |  | Other | N/F
3010 | 3010 | Y | Office | 092 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and black streaks | [6 empty] | PLEL | NS as the material was visually similar to S002.
3010 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and black streaks | [7 empty] | NS as the material was visually similar to S002
3010 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 480 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S044 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3010 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S013
3010 |  |  |  |  | Piping | N/F
3010 |  |  |  |  | Mechanical | N/F
3010 |  |  |  |  | Other | N/F
3011 | 3011 | Y | Office | 091 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040.
3011 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S040.
3011 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJc | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3011 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3011 |  |  |  |  | Piping | N/F
3011 |  |  |  |  | Mechanical | N/F
3011 |  |  |  |  | Other | N/F
3011A | 3011 | Y | Office | 091 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040.
3011A |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S040.
3011A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3011A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3011A |  |  |  |  | Piping | N/F
3011A |  |  |  |  | Mechanical | N/F
3011A |  |  |  |  | Other | N/F
3012 | 3012 | Y | Office | 089 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
3012 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 170 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3012 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3012 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 9 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3012 |  |  |  |  | Mechanical | N/F
3012 |  |  |  |  | Other | N/F
3013 | 3013 | Y | Office | 090 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
3013 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 170 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3013 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3013 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3013 |  |  |  |  | Mechanical | N/F
3013 |  |  |  |  | Other | N/F
3013A | 3013A | Y | Office |  | Floor | Tile | Vinyl tile | NS | [6 empty] | VS009 | 12' x 12' Blue with abundant dark blue and white flecks | [6 empty] | PLEL
3013A |  |  |  |  | Wall | Wood |  | NS | [15 empty] | NS as the material is not suspect ACM
3013A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 750 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3013A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | [7 empty] | VS031 | 2' x 4' with 1" square pattern
3013A |  |  |  |  | Piping | N/F
3013A |  |  |  |  | Mechanical | N/F
3013A |  |  |  |  | Other | N/F
3013B | 3013B | Y | Office |  | Floor | Tile | Vinyl tile | NS | [6 empty] | VS009 | 12' x 12' Blue with abundant dark blue and white flecks | [6 empty] | PLEL
3013B |  |  |  |  | Wall | Wood |  | NS | [15 empty] | NS as the material is not suspect ACM
3013B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 750 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3013B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | [7 empty] | VS031 | 2' x 4' with 1" square pattern
3013B |  |  |  |  | Piping | N/F
3013B |  |  |  |  | Mechanical | N/F
3013B |  |  |  |  | Other | N/F
3014 | 3014 | Y | Office | 088 | Floor | Tile | Vinyl tile | N | [6 empty] | S043 | 12' x 12' White with black streaks | [6 empty] | PLEL | No mastic analyzed.
3014 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3014 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3014 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 8 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3014 |  |  |  |  | Mechanical | N/F
3014 |  |  |  |  | Other | N/F
3015 | 3015 | Y | Office | 087 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3015 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S040
3015 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3015 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3015 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 8 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3015 |  |  |  |  | Mechanical | N/F
3015 |  |  |  |  | Other | N/F
3016 | 3016 | Y | Office | 086 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3016 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S040
3016 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S042 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3016 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3016 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 9 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3016 |  |  |  |  | Mechanical | N/F
3016 |  |  |  |  | Other | N/F
3017 | 3017 | Y | Office | 085 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3017 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S040
3017 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3017 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3017 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 7 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3017 |  |  |  |  | Mechanical | N/F
3017 |  |  |  |  | Other | N/F
3018 | 3018 | Y | Office | 084 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3018 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S040
3018 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3018 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3018 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 9 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3018 |  |  |  |  | Mechanical | N/F
3018 |  |  |  |  | Other | N/F
3019 | 3019 | Y | Office | 083 | Floor | Tile | Vinyl tile | N | [6 empty] | S041 | 12' x 12' White with brown flecks | [6 empty] | PLEL
3019 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S041 | 12' x 12' White with brown flecks
3019 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3019 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3019 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 8 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3019 |  |  |  |  | Mechanical | N/F
3019 |  |  |  |  | Other | N/F
3020 | 3020 | Y | Office | 082 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3020 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3020 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3020 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 8 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3020 |  |  |  |  | Mechanical | N/F
3020 |  |  |  |  | Other | N/F
3021 | 3021 | Y | Office | 139 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040.
3021 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S040.
3021 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3021 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3021 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 7 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3021 |  |  |  |  | Mechanical | N/F
3021 |  |  |  |  | Other | N/F
3022 | 3022 | Y | Office | 081 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3022 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3022 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3022 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 7 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3022 |  |  |  |  | Mechanical | N/F
3022 |  |  |  |  | Other | N/F
3023 | 3023 | Y | Office | 080 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3023 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3023 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3023 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 9 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3023 |  |  |  |  | Mechanical | N/F
3023 |  |  |  |  | Other | N/F
3024 | 3024 | Y | Office | 079 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3024 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3024 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3024 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 9 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3024 |  |  |  |  | Mechanical | N/F
3024 |  |  |  |  | Other | N/F
3025 | 3025 | Y | Office | 078 | Floor | Tile | Vinyl tile | N | [6 empty] | S040 | 12' x 12' White with brown streaks | [6 empty] | PLEL
3025 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S040 | 12' x 12' White with brown streaks
3025 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3025 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3025 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 9 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3025 |  |  |  |  | Mechanical | N/F
3025 |  |  |  |  | Other | N/F
3026 | 3026 | Y | Office | 077 | Floor | Tile | Vinyl tile | N | [6 empty] | S039 | 12' x 12' Light brown with abundant brown fleck | [6 empty] | PLEL
3026 |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S039 | 12' x 12' Light brown with abundant brown fleck
3026 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | Sf | 320 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3026 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3026 |  |  |  |  | Piping | N/F
3026 |  |  |  |  | Mechanical | N/F
3026 |  |  |  |  | Other | N/F
3026A | 3026 | Y | Office | 076 | Floor | Tile | Vinyl tile | N | [6 empty] | S038 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL
3026A |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S038 | 12' x 12' White with abundant grey flecks
3026A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 144 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3026A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3026A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3026A |  |  |  |  | Mechanical | N/F
3026A |  |  |  |  | Other | N/f
3027 | 3027 | Y | Office | 102 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
3027 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3027 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3027 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | p | D | N | EA | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3027 |  |  |  |  | Mechanical | N/F
3027 |  |  |  |  | Other | N/f
3028 | 3028 | Y | Office | 101 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3028 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3028 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3028 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | p | D | N | EA | 8 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3028 |  |  |  |  | Mechanical | N/F
3028 |  |  |  |  | Other | N/f
3029 | 3029 | Y | Office | 100 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3029 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3029 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3029 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | p | D | N | EA | 10 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3029 |  |  |  |  | Mechanical | N/F
3029 |  |  |  |  | Other | N/f
3030 | 3030 | Y | Office | 099 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3030 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually simialr to S040
3030 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 170 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3030 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3030 |  |  |  |  | Piping | M
3030 |  |  |  |  | Mechanical | N/F
3030 |  |  |  |  | Other | N/F
3031 | 3031 | Y | Office | 098 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3031 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually simialr to S040
3031 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 170 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3031 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3031 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 12 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3031 |  |  |  |  | Mechanical | N/F
3031 |  |  |  |  | Other | N/F
3032 | 3032 | Y | Office | 096 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3032 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually simialr to S040
3032 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3032 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3032 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 12 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3032 |  |  |  |  | Mechanical | N/F
3032 |  |  |  |  | Other | N/F
3033 | 3033 | Y | Office | 095 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3033 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually simialr to S040
3033 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3033 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3033 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 8 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3033 |  |  |  |  | Mechanical | N/F
3033 |  |  |  |  | Other | N/F
3034 | 3034 | Y | Office | 094 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3034 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually simialr to S040
3034 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3034 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3034 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 11 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3034 |  |  |  |  | Mechanical | N/F
3034 |  |  |  |  | Other | N/F
3035 | 3035 | Y | Office | 093 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S040
3035 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS040 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually simialr to S040
3035 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3035 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
3035 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 7 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3035 |  |  |  |  | Mechanical | N/F
3035 |  |  |  |  | Other | N/F
3036 | 3036 | Y | Office | 097 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and blacks streaks | [6 empty] | PLEL | NS as the material was visually similar to S002.
3036 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and black streaks | [7 empty] | NS as the material was visually similar to S002.
3036 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3036 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3036 |  |  |  |  | Piping | N/F
3036 |  |  |  |  | Mechanical | N/F
3036 |  |  |  |  | Other | N/F
3037 | 3037 | Y | Classroom |  | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3037 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1200 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material is similar to another sample
3037 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | [7 empty] | VS031 | 2' x 4' with 1" square pattern
3037 |  |  |  |  | Piping | Straight line | Tar mastic | P | A | N | SF | 60 | - | - | VS014 | Tar Mastic | 10 | 0 | 0 | 0 | 0 | 0
3037 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork
3037 |  |  |  |  | Other | N/F
3037A | 3037 | Y | Office | 051 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
3037A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3037A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3037A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3037A |  |  |  |  | Mechanical | N/F
3037A |  |  |  |  | Other | N/F | [17 empty] | Limited access above ceiling
3037B | 3037 | Y | Office | 052 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
3037B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3037B |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3037B |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3037B |  |  |  |  | Mechanical | N/F
3037B |  |  |  |  | Other | N/F | [17 empty] | Limited access above ceiling
3038 | 3038 | Y | Office | 053 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3038 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3038 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole and small fissure | [7 empty] | NS as the material was visually the same as S028.
3038 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3038 |  |  |  |  | Mechanical | N/F
3038 |  |  |  |  | Other | N/F
3038A | 3038 | Y | Office | 103 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3038A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3038A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3038A |  |  |  |  | Piping | N/F
3038A |  |  |  |  | Mechanical | N/F
3038A |  |  |  |  | Other | N/f
3038B | 3038 | Y | Office | 104 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
3038B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3038B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3038B |  |  |  |  | Piping | N/F
3038B |  |  |  |  | Mechanical | N/F
3038B |  |  |  |  | Other | N/f
3038C | 3038C | Y | Office | 105 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and blacks streaks | [6 empty] | PLEL | NS as the material was visually similar to S002.
3038C |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and black streaks | [7 empty] | NS as the material was visually similar to S002.
3038C |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S045 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3038C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3038C |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3038C |  |  |  |  | Mechanical | N/F
3038C |  |  |  |  | Other | N/F
3C01 |  | Y | Hallway | 046 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
3C01 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
3C01 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S029 was collected but not confirmed ACM.S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3C01 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3C01 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S028 | 2' x 2' pinhole and small fissure
3C01 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 25 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3C01 |  |  |  |  | Mechanical | N/F
3C01 |  |  |  |  | Other | N/F
3C02 |  | Y | Hallway | 048 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
3C02 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
3C02 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3C02 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole and small fissure | [7 empty] | NS as the material was visually similar to S028
3C02 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 25 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3C02 |  |  |  |  | Mechanical | N/F
3C02 |  |  |  |  | Other | N/F
3S02 |  | Y | Stairwell | 162 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
3S02 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3S02 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3S02 |  |  |  |  | Piping | N/F
3S02 |  |  |  |  | Mechanical | N/F
3S02 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
3S03 |  | Y | Stairwell | 164 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS043 | 12' x 12' White with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S043. No mastic analyzed.
3S03 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
3S03 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS013 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S013.
3S03 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | p | D | N | EA | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
3S03 |  |  |  |  | Mechanical | N/F
3S03 |  |  |  |  | Other | N/F
3E01 |  | Y | Elevator | 165 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS041 | 12' x 12' White with brown flecks | [6 empty] | PLEL | NS as the material was visually similar to S041.
3E01 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS041 | 12' x 12' White with brown flecks | [7 empty] | NS as the material was visually similar to S041
3E01 |  |  |  |  | Wall |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
3E01 |  |  |  |  | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
3E01 |  |  |  |  | Piping | N/F
3E01 |  |  |  |  | Mechanical | N/F
3E01 |  |  |  |  | Other | N/F
4000 | 4000 | Y | Boardroom | 058 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4000 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 1000 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S034 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4000 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS031 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually the same as S031.
4000 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 4 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4000 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 10 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4000 |  |  |  |  | Mechanical | N/F
4000 |  |  |  |  | Other | N/F
4001 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4001 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4001 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4001 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4001 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4001 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4001 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4001 |  |  |  |  | Other | N/f
4002 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4002 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4002 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4002 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4002 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4002 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4002 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4002 |  |  |  |  | Other | N/f
4003 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4003 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4003 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4003 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4003 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4003 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4003 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4003 |  |  |  |  | Other | N/f
4004 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4004 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4004 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4004 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4004 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4004 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4004 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4004 |  |  |  |  | Other | N/f
4005 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4005 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4005 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4005 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4005 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4005 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4005 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4005 |  |  |  |  | Other | N/f
4006 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4006 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4006 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4006 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4006 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4006 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4006 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4006 |  |  |  |  | Other | N/f
4007 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4007 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4007 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4007 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4007 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4007 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4007 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4007 |  |  |  |  | Other | N/f
4008 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4008 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4008 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4008 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4008 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4008 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4008 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4008 |  |  |  |  | Other | N/f
4009 | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4009 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4009 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4009 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4009 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4009 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4009 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4009 |  |  |  |  | Other | N/f
4009A | 4001 - 4009 | Y | Office | 057 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4009A |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4009A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S033 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4009A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually similar to S028.
4009A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS032 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S032.
4009A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 15 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4009A |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024
4009A |  |  |  |  | Other | N/f
4010 | 4010 | Y | Storage |  | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as the material is not suspect ACM
4010 |  |  |  |  | Wall |  | Concrete | NS | [15 empty] | NS as the material is not suspect ACM
4010 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM; combined with 4010A
4010 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 750 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM; combined with 4010A
4010 |  |  |  |  | Ceiling
4010 |  |  |  |  | Piping | N/F | [6 empty] | - | -
4010 |  |  |  |  | Mechanical | N/F
4010 |  |  |  |  | Other | N/f
4010A | 4010 | Y | Storage |  | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as the material is not suspect ACM
4010A |  |  |  |  | Wall |  | Concrete | NS | [15 empty] | NS as the material is not suspect ACM
4010A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM; combined with 4010
4010A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 750 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM; combined with 4010
4010A |  |  |  |  | Ceiling
4010A |  |  |  |  | Piping | N/F | [6 empty] | - | -
4010A |  |  |  |  | Mechanical | N/F
4010A |  |  |  |  | Other | N/f
4011 | 4011 | Y | Office | 056 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL | NS as the material was visually similar to S022.
4011 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink | [7 empty] | NS as the material was visually similar to S022.
4011 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4011 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS031 | 2' x 4' with 1" square pattern | [7 empty] | NS as the material was visually the same as S031.
4011 |  |  |  |  | Piping | Sink | Tar mastic | P | D | N | SF | 3 | - | - | VS032 | Gold tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S032.
4011 |  |  |  |  | Mechanical | N/F
4011 |  |  |  |  | Other | N/F
4012 | 4012 | Y | Office | 055 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S002
4012 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and grey flecks | [7 empty] | NS as the material was visually similar to S002
4012 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4012 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4012 |  |  |  |  | Piping | Sink | Tar mastic | Y | D | N | SF | 9 | - | - | S032 | Gold tar mastic on sink | 5 | 0 | 0 | 0 | 0 | 0
4012 |  |  |  |  | Mechanical | N/F
4012 |  |  |  |  | Other | N/f | [17 empty] | No access above ceiling.
4013 | 4013 | Y | Office | 054 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS022 | 12' x 12' Pink | [6 empty] | PLEL | NS as the material was visually similar to S022.
4013 |  |  |  |  | Floor | Tile | Tile mastic | NS | [6 empty] | VS022 | 12' x 12' Pink | [7 empty] | NS as the material was visually similar to S022.
4013 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4013 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S031 | 2' x 4' with 1" square pattern
4013 |  |  |  |  | Piping | N/F
4013 |  |  |  |  | Mechanical | N/F
4013 |  |  |  |  | Other | N/F
4014 | 4014 | Y | Office | 071 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4014 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4014 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4014 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4014 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024.
4014 |  |  |  |  | Other | N/F
4014A | 4014 | Y | Office | 071 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4014A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4014A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4014A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4014A |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024.
4014A |  |  |  |  | Other | N/F
4014B | 4014 | Y | Office | 070 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4014B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4014B |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4014B |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4014B |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024.
4014B |  |  |  |  | Other | N/F
4014C | 4014 | Y | Office | 072 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4014C |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4014C |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4014C |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4014C |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024.
4014C |  |  |  |  | Other | N/F
4014D | 4014 | Y | Office | 073 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4014D |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4014D |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4014D |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4014D |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024.
4014D |  |  |  |  | Other | N/F
4015 | 4015 | Y | Office | 149 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4015 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 180 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4015 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4015 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4015 |  |  |  |  | Mechanical | N/F
4015 |  |  |  |  | Other | N/F
4016 | 4016 | Y | Office | 150 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4016 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4016 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4016 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4016 |  |  |  |  | Mechanical | N/F
4016 |  |  |  |  | Other | N/F
4017 | 4017 | Y | Office | 151 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4017 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4017 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4017 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4017 |  |  |  |  | Mechanical | N/F
4017 |  |  |  |  | Other | N/F
4018 | 4018 | Y | Office | 152 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4018 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4018 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4018 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4018 |  |  |  |  | Mechanical | N/F
4018 |  |  |  |  | Other | N/F
4018A | 4018 | Y | Office | 153 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4018A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4018A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4018A |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4018A |  |  |  |  | Mechanical | N/F
4018A |  |  |  |  | Other | N/F
4019 | 4019 | Y | Office | 074 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4019 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4019 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4019 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4019 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024.
4019 |  |  |  |  | Other | N/F
4020 | 4020 | Y | Office | 154 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4020 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4020 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4020 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4020 |  |  |  |  | Mechanical | N/F
4020 |  |  |  |  | Other | N/F
4021 | 4021 | Y | Office | 155 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4021 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4021 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4021 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4021 |  |  |  |  | Mechanical | N/F
4021 |  |  |  |  | Other | N/F
4022 | 4022 | Y | Office | 156 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4022 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4022 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4022 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4022 |  |  |  |  | Mechanical | N/F
4022 |  |  |  |  | Other | N/F
4023 | 4023 | Y | Office | 157 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4023 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4023 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4023 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 9 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4023 |  |  |  |  | Mechanical | N/F
4023 |  |  |  |  | Other | N/F
4024 | 4024 | Y | Office | 063 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4024 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4024 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS031 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S031
4024 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 7 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4024 |  |  |  |  | Mechanical | N/F
4024 |  |  |  |  | Other | N/F
4024A | 4024 | Y | Office | 059 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
4024A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4024A |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | Sf | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4024A |  |  |  |  | Piping | N/F
4024A |  |  |  |  | Mechanical | N/F
4024A |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
4024B | 4024 | Y | Office | 060 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
4024B |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4024B |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | Sf | 100 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4024B |  |  |  |  | Piping | N/F
4024B |  |  |  |  | Mechanical | N/F
4024B |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
4024C | 4024 | Y | Office | 061 | Floor | Tile | Vinyl tile | N | [6 empty] | S035 | 12' x 12' Yellow | [6 empty] | PLEL
4024C |  |  |  |  | Floor | Tile | Tile mastic | N | [6 empty] | S035 | 12' x 12' Yellow
4024C |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 70 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4024C |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | Sf | 70 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4024C |  |  |  |  | Piping | N/F
4024C |  |  |  |  | Mechanical | N/F
4024C |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
4025 | 4025 | Y | Office | 159 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4025 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4025 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4025 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4025 |  |  |  |  | Mechanical | N/F
4025 |  |  |  |  | Other | N/F
4026 | 4026 | Y | Office | 160 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4026 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4026 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4026 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4026 |  |  |  |  | Mechanical | N/F
4026 |  |  |  |  | Other | N/F
4027 | 4026 | Y | Office | 160 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4027 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4027 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS019 | 2' x 4' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S019
4027 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4027 |  |  |  |  | Mechanical | N/F
4027 |  |  |  |  | Other | N/F
4028 | 4028 | Y | Office | 064 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4028 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4028 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS031 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S031
4028 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4028 |  |  |  |  | Mechanical | N/F
4028 |  |  |  |  | Other | N/F
4029 | 4029 | Y | Office | 065 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4029 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4029 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS031 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S031
4029 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 6 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4029 |  |  |  |  | Mechanical | N/F
4029 |  |  |  |  | Other | N/F
4030 | 4030 | Y | Office | 068 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4030 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 144 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4030 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS031 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S031
4030 |  |  |  |  | Piping | N/F
4030 |  |  |  |  | Mechanical | N/F
4030 |  |  |  |  | Other | N/F
4031 | 4032 | Y | Office | 067 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4031 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4031 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhle and small fissure | [7 empty] | NS as the material was visually similar to S028
4031 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4031 |  |  |  |  | Mechanical | N/F
4031 |  |  |  |  | Other | N/F
4032 | 4032 | Y | Office | 067 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4032 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4032 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhle and small fissure | [7 empty] | NS as the material was visually similar to S028
4032 |  |  |  |  | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 5 | - | - | VS014 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
4032 |  |  |  |  | Mechanical | N/F
4032 |  |  |  |  | Other | N/F
4033 | 4033 | Y | Office | 066 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
4033 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 144 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4033 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS031 | 2' x 2' with 1" square pattern | [7 empty] | NS as the material was visually similar to S031
4033 |  |  |  |  | Piping | N/F
4033 |  |  |  |  | Mechanical | N/F
4033 |  |  |  |  | Other | N/F
4033A | 4033 | Y | Office | 062 | Floor | Sheet Flooring | VSF | N | [6 empty] | S036 | Blue with white mottling | [6 empty] | PLEL
4033A |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4033A |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4033A |  |  |  |  | Piping | SInk | Tar mastic | P | D | N | SF | 3 | - | - | VS022 | Gold tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
4033A |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic | [7 empty] | NS as the material was visually similar to S024
4033A |  |  |  |  | Other | N/F
4034 | 4034 | Y | Office | 069 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS002 | Grey with large white and black streaks | [6 empty] | PLEL | NS as the material was visually similar to S002.
4034 |  |  |  |  | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS002 | Grey with large white and black streaks | [7 empty] | NS as the material was visually similar to S002
4034 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 110 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S037 was collected but not confirmed ACM. S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4034 |  |  |  |  | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS028 | 2' x 2' pinhole with small fissure | [7 empty] | NS as the material was visually the same as S028.
4034 |  |  |  |  | Piping | N/F
4034 |  |  |  |  | Mechanical | Ductwork | Tar mastic | NS | [6 empty] | VS024 | Tar mastic on ductwork | [7 empty] | NS as the material was visually similar to S024.
4034 |  |  |  |  | Other | N/F
4035 | 4035 | Y |  |  | Floor |  | CLAY TILE | NS | [15 empty] | NS as terazzo is not suspect ACM.
4035 |  |  |  |  | Wall | Drywall | DWJC | P | C | N | SF | 160 |  |  | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 | 0 | AS PER S007
4035 |  |  |  |  | Ceiling | Drywall | DWJC | P | C | N | SF | 100 |  |  | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 | 0 | AS PER S007
4035 |  |  |  |  | Piping | N/F
4035 |  |  |  |  | Mechanical | N/F
4035 |  |  |  |  | Other | N/F | [17 empty] | No acces above the ceiling.
4C01 |  | Y | Hallway | 075 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
4C01 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4C01 |  |  |  |  | Ceiling | Panel | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
4C01 |  |  |  |  | Piping | N/F
4C01 |  |  |  |  | Mechanical | N/F
4C01 |  |  |  |  | Other | N/F | [17 empty] | No access above ceiling.
4S03 |  | Y | Stairwell | 161 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
4S03 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4S03 |  |  |  |  | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4S03 |  |  |  |  | Piping | N/F
4S03 |  |  |  |  | Mechanical | N/F
4S03 |  |  |  |  | Other | N/F | [17 empty] | No access above the ceiling.
4C02 | 4C02 | Y | Hallway |  | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
4C02 |  |  |  |  | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S015 was confirmed ACM; therefore all DWJC should be considered ACM.
4C02 |  |  |  |  | Ceiling |  | Steel | NS
4C02 |  |  |  |  | Piping | N/F
4C02 |  |  |  |  | Mechanical | N/F
4C02 |  |  |  |  | Other | N/F