## Sheet1
Building | Room # | Room # (numeric) | Room Accessed (Y/N) | Location Description | PLEL Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[12 empty] | Unit of Measure | Condition
[13 empty] | Good | Fair | Poor
C | 1004 | 1004 | Y | Office | 001 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S001 | 2' x 2' pinhole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1002 | 1002 | N | Office | 002 | Floor | [17 empty] | PLEL
Wall
Ceiling
Piping
Mechanical
[6 empty] | Other | [18 empty] | No access.
C | 1005 | 1005 | Y | Office | 003 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1003 | 1003 | Y | Office | 004 | Floor | Sheet Flooring | VSF | N | [6 empty] | S002 | Green VSF | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S002 | Green VSF
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S004 | 2' x 2' grey finish
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Sheet Flooring | VSF Mastic | N | [6 empty] | S003 | Black VSF
[6 empty] | Other | Sheet Flooring | VSF | N | [6 empty] | S003 | Black VSF
C | 1007 | 1007 | Y | Office | 005 | Floor | Tile | Vinyl tile | N | [6 empty] | S005 | 12' x 12' Grey with black streak | [6 empty] | PLEL | Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS001 | 2'x2' pinhole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Acoustic tile | Lay-in T-bar | N | [6 empty] | S006 | 2' x 2' pinhole fleck
C | 1006 | 1006 | Y | Office | 006 | Floor | Tile | Vinyl tile | Y | A | N | SF | 390 | - | 10 | S007 | 12' x 12' White with long black streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S007 | 12' x 12' White with long black streak
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1C02 |  | Y | Corridor | 007 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1009 | 1009 | Y | Office | 008 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1010 | 1010 | Y | Office | 009 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1000 B | 1000 | Y | Corridor | 010 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 1170 | - | - | S008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | Y | EA | 8 | - | - | VS016 | tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually simialr to S009.
C | 1040 | 1040 | Y | Classroom | 011 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material was visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 360 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Exterior Wall | Tar mastic | P | D | N | SF | 400 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
C | 1040 A | 1040 | Y | Classroom | 012 | Floor | Tile | Vinyl tile | N | [6 empty] | S011 | 12' x 12' White with black streak | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S011 | 12' x 12' White with black streak
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 360 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Exterior Wall | Tar mastic | Y | D | N | SF | 200 | - | - | S010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0
C | 1042 | 1042 | Y | Office | 013 | Floor | Sheet Flooring | VSF | Y | A | N | SF | 200 | - | - | S012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Exterior Wall | Tar mastic | P | D | N | Sf | 100 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
C | 1044 | 1044 | Y | Office | 014 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall |  | Plaster | N | [6 empty] | S013 | Plaster under window
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Exterior Wall | Tar mastic | P | D | N | Sf | 100 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
C | 1046 | 1046 | Y | Office | 015 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1050 | 1050 | Y | Office | 016 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material was visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Column | Decorative Coating | Y | A | Y | SF | 80 | - | - | S014 | Texture on column (DWJC behind decorative cotain wall column) | 2 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Exterior Wall | Tar mastic | P | D | N | SF | 200 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
C | 1051 | 1051 | Y | Office | 017 | Floor | Sheet Flooring | VSF | N | [6 empty] | S015 | Grey with white and dark speck | [6 empty] | PLEL | Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Elbows/Fittings | Tar mastic | Y | D | N | EA | 4 | - | - | S016 | Tar mastic above ceiling | 10 | 0 | 0 | 0 | 0 | 0
C | 1052 | 1052 | Y | Office | 018 | Floor | Sheet Flooring | VSF | P | A | N | SF | 900 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Wall | Column | Decorative Coating | P | A | Y | SF | 20 | - | - | VS014 | Texture on column | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
[6 empty] | Wall | Exterior Wall | Tar mastic | P | D | N | SF | 300 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
Ceiling
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 1053 | 1053 | Y | Office | 019 | Floor | Sheet Flooring | VSF | P | A | N | SF | - | - | 900 | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1100 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S017 was collected in this room but was not ACM however S008 of DWJC was confirmed ACM; therefore all DWJC is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Sheet Flooring | VSF | Y | A | N | SF | 100 | - | - | S018 | Brick pattern VSF | 15 | 0 | 0 | 0 | 0 | 0
C | 1051 A | 1051 | Y | Office | 020 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1058 | 1058 | Y | Office | 021 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Fume Hood | Transite | P | D | N | SF | 30 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the equipment was running. Visually the same as S021.
C | 1059 | 1059 | Y | Office | 022 | Floor | Sheet Flooring | VSF | Y | A | N | Sf | 160 | - | - | S019 | Light green stone | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | Unable to separate mastic.
[6 empty] | Wall |  | Plaster | NS | [6 empty] | VS013 | Plaster under window | [7 empty] | NS as the material was visually similar to S013.
[6 empty] | Wall | Exterior Wall | Tar mastic | P | D | N | SF | 100 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 30 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 1056 | 1056 | Y | Office | 023 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS004 | 2' x 2' grey | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Piping | [18 empty] | No access above ceiling.
[6 empty] | Mechanical | [18 empty] | No access above ceiling.
[6 empty] | Other | [18 empty] | No access above ceiling.
C | 1060 | 1060 | Y | Office | 024 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F | [17 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 1057 | 1057 | Y | Office | 025 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Plaster | NS | [6 empty] | VS013 | Plaster under window | [7 empty] | NS as the material is visually similar to S013.
[6 empty] | Wall | Exterior Wall | Tar mastic | P | D | N | SF | 60 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material is visually similar to S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 1061 | 1061 | Y | Office | 026 | Floor | Tile | Vinyl tile | N | [6 empty] | S020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S020 | 12' x 12' White with abundant grey flecks
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Exterior Wall | Tar mastic | P | D | N | SF | 100 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 1062 | 1062 | Y | Office | 027 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Plaster | NS | [6 empty] | VS013 | Plaster under window | [7 empty] | NS as the material was visually similar to S013.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Sink | Tar | Y | A | N | SF | 2 | - | 2 | S022 | Black tar under sink | 10 | 0 | 0 | 0 | 0 | 0
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | Y | A | N | SF | 30 | - | - | S021 | Transite | 20 | 0 | 0 | 0 | 0 | 0
C | 1063 | 1063 | Y | Office | 028 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Exterior Wall | Tar mastic | P | A | N | SF | 100 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
[6 empty] | Wall | Column | Decorative Coating | P | A | Y | SF | 15 | - | - | VS014 | Texture on column | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S014.
[6 empty] | Wall | Window sill | Plaster debris | N | [6 empty] | S023 | Plaster debris
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | [8 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Other | N/F
C | 1064 | 1064 | Y | Office | 029 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material did not use DWJC.
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1066 | 1066 | Y | Office | 030 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S020.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020/
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1068 | 1068 | Y | Office | 031 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood fibre is not suspect ACM>
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 2051 | 2051 | Y | Office | 032 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S020.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 2048 | 2048 | Y | Office | 033 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 170 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2046 | 2046 | Y | Office | 034 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually the same as S020.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 170 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2037 | 2037 | Y | Office | 035 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually the same as S020.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar as S020
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 2032 | 2032 | Y | Office | 036 | Floor | Sheet Flooring | VSF | N | [6 empty] | S024 | Light brown VSF | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S024 | Light brown VSF
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 320 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 2031 | 2031 | Y | Classroom | 037 | Floor | Sheet Flooring | VSF | N | [6 empty] | S025 | Light brown with brown fleck | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S025 | Light brown with brown fleck
[6 empty] | Floor | Sheet Flooring | VSF | N | [6 empty] | S027 | Blue with dark blue wave
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S027 | Blue with dark blue wave
[6 empty] | Floor | Sheet Flooring | VSF | P | A | N | SF | 140 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 4200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S026 was collected in this room but ACM was not confirmed. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 12 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Sheet Flooring | VSF | NS | [15 empty] | Grey VSF was new as of 2008 and not sampled.
C | 1067 A | 1067 | Y | Office | 038 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Wall | Plaster | N | [6 empty] | S028 | Wall plaster
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | - | - | 4 | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
C | 2036 | 2036 | Y | Classroom | 039 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2034 | 2034 | Y | Office | 040 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2040 | 2040 | Y | Office | 041 | Floor | Sheet Flooring | VSF | N | [6 empty] | S029 | Grey with blue streaks | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S029 | Grey with blue streaks
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/f
C | 3000 | 3000 | Y | Office | 042 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3001 | 3001 | Y | Office | 043 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 30 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Wall | Plaster | N | [6 empty] | S030 | Wall plaster
C | 3002A, 3002B, 3002C | 3002 | Y | Office | 044 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS025 | Light brown with brown fleck | [6 empty] | PLEL | NS as the material was visually similar to S025.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS025 | Light brown with brown fleck | [7 empty] | NS as the material was visually similar to S025.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S031 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3005, 3005 A, 3005 B, 3005 C, 3005 D, 3005 E | 3005 | Y | Office | 045 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS025 | Light brown with brown fleck | [6 empty] | PLEL | NS as the material was visually similar to S025.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS025 | Light brown with brown fleck | [7 empty] | NS as the material was visually similar to S025.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3003 | 3003 | Y | Office | 046 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/f
C | 3004 | 3004 | Y | Office | 047 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material was visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3007 | 3007 | Y | Office | 048 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS025 | Light brown with brown flecks | [6 empty] | PLEL | NS as the material was visually similar to S025.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS025 | Light brown with brown flecks | [7 empty] | NS as the material was visually similar to S025.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3008 | 3008 | Y | Washroom | 049 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 3010 | 3010 | Y | Washroom | 050 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 3011 | 3011 | Y | Office | 051 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3012 | 3012 | Y | Office | 052 | Floor | Sheet Flooring | VSF | P | A | N | SF | 170 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/f
C | 3014 | 3014 | Y | Office | 053 | Floor | Sheet Flooring | VSF | P | A | N | SF | 170 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3015 | 3015 | Y | Office | 054 | Floor | Sheet Flooring | VSF | P | A | N | SF | 170 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3016 | 3016 | Y | Office | 055 | Floor | Sheet Flooring | VSF | P | A | N | SF | 170 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3017 | 3017 | Y | Office | 056 A | Floor | Sheet Flooring | VSF | P | A | N | SF | 170 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3018 | 3018 | Y | Office | 056 B | Floor | Sheet Flooring | VSF | P | A | N | SF | 170 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3020 | 3020 | Y | Office | 057 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Other | N/F
C | 3022 | 3022 | Y | Office | 058 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material was visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 190 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3023 | 3023 | Y | Office | 059 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS019 | Light green stone | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S019. Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simialr to S016.
C | 3024 | 3024 | Y | Office | 060 | Floor | Sheet Flooring | VSF | P | A | N | SF | 600 | - | - | VS019 | Light green stone | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S019. Unable to separate mastic.
[6 empty] | Wall | Wall | Plaster | N | [6 empty] | S032 | Wall plaster
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F | [17 empty] | Limited access above the ceiling.
C | 3025 | 3025 | Y | Office | 061 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Other | N/F
C | 3026 | 3026 | Y | Office | 062 | Floor |  | Carpet | NS | [14 empty] | PLEL
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 190 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3027 | 3027 | Y | Office | 063 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material is visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 190 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3028 | 3028 | Y | Office | 064 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 450 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 3029 | 3029 | Y | Office | 065 | Floor | Tile | Vinyl tile | N | [6 empty] | S033 | 12' x 12' Light grey with abundant white and grey flecks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S033 | 12' x 12' Light grey with abundant white and grey flecks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 190 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S034 | 2' x 2' pinhole and hole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 3030 | 3030 | Y | Office | 066 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S035 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS016 | Tar mastic | 10 | - | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 3031 | 3031 | Y | Office | 067 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material was visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 190 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3051 | 3051 | Y | Male Washroom | 068 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 3054 A | 3054 | Y | Office | 069 | Floor | Sheet Flooring | VSF | N | [6 empty] | S036 | Green with wave | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S036 | Green with wave
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Sheet Flooring | VSF | P | A | N | SF | 130 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S012.
C | 3057 | 3057 | Y | Office | 070 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS036 | Green with wave | [6 empty] | PLEL | NS as the material was visually similar to S036.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS036 | Green with wave | [7 empty] | NS as the material was visually similar to S036.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | [7 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3058 | 3058 | Y | Office | 071 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material was visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | Vs009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 3060 | 3060 | Y | Office | 072 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [6 empty] | PLEL | NS as the material was visually similar to S011.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS011 | 12' x 12' White with black streak | [7 empty] | NS as the material was visually similar to S011.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | Vs009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 3061 | 3061 | Y | Office | 073 | Floor | Sheet Flooring | VSF | N | [6 empty] | S047 | Green wave | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S047 | Green wave
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material is visually similar to S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material is visually similar to S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS016 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
C | 3061 A | 3061 | Y |  | 074 | Floor | [17 empty] | PLEL
Wall
Ceiling
Piping
Mechanical
[6 empty] | Other | [18 empty] | No access.
C | 3C05 |  | Y | Hallway | 075 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S037 | 2' x 4' pinhole
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3C04 |  | Y | Hallway | 076 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Girders above ceiling | Spray fireproofing | Y | D | Y | Sf | 220 | - | - | S038 | Spray fireproofing | 0 | 0 | 0 | 35 | 0 | 0 |  | The material is isolated using plastic sheeting and absestos warning signs.
C | 3C03 |  | Y | Hallway | 077 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3C02 |  | Y | Hallway | 078 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Ceiling | Girders above ceiling | Spray fireproofing | P | D | Y | Sf | 1050 | - | - | VS038 | Spray fireproofing | 0 | 0 | 0 | 35 | 0 | 0 |  | NS as the material was visually similar to S038.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 3C01 |  | Y | Hallway | 079 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Ceiling | Girders above ceiling | Spray fireproofing | P | D | Y | Sf | 1300 | - | - | VS038 | Spray fireproofing | 0 | 0 | 0 | 35 | 0 | 0 |  | NS as the material was visually similar to S038.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/f
C | 3062 | 3062 | Y | Office | 080 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3064 | 3064 | Y | Washroom | 081 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Tile | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3070 | 3070 | Y | Office | 082 | Floor | Tile | Vinyl tile | N | [6 empty] | S039 | 12' x 12' White with abundant brown flecks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S039 | 12' x 12' White with abundant brown flecks
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | A | N | EA | 1 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 3071 | 3071 | Y | Office | 083 | Floor | Sheet Flooring | VSF | NS | [14 empty] | PLEL | NS as the material is new.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material is visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 8 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material is visually similar to S016.
C | 3071 A | 3071 | Y | Office | 084 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4042 | 4042 | Y | Office | 085 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4041 | 4041 | Y | Washroom | 086 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 4043 | 4043 | Y | Office | 087 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [6 empty] | PLEL | NS as the material was visually similar to S029.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS029 | Grey with blue fleck | [7 empty] | NS as the material was visually similar to S029.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/f
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4043 B, 4043 C | 4043 | Y | Office | 088 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [6 empty] | PLEL | NS as the material was visually similar to S029.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [7 empty] | NS as the material was visually similar to S029.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4045 | 4045 | Y | Office | 089 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [6 empty] | PLEL | NS as the material was visually similar to S029.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [7 empty] | NS as the material was visually similar to S029.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 4047 | 4047 | Y | Office | 090 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [6 empty] | PLEL | NS as the material was visually similar to S029.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [7 empty] | NS as the material was visually similar to S029.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4049 | 4049 | Y | Office | 091 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [6 empty] | PLEL | NS as the material was visually similar to S029.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [7 empty] | NS as the material was visually similar to S029.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4051 | 4051 | Y | Office | 092 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4053 | 4053 | Y | Office | 093 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4055 | 4055 | Y | Office | 094 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | S040 | 2' x 2' textured pinhole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4056 | 4056 | Y | Office | 095 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [6 empty] | PLEL | NS as the material was visually similar to S029.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS029 | Grey with blue fleck | [7 empty] | NS as the material was visually similar to S029.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/f | [17 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 4057 | 4057 | Y | Office | 096 | Floor | Sheet Flooring | VSF | N | [6 empty] | S041 | Cream VSF | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S041 | Cream VSf
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | Vs001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F | [17 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | N/F | [17 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4058 | 4058 | Y | Office | 097 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4059 | 4059 | Y | Office | 098 | Floor | Sheet Flooring | VSF | N | [6 empty] | S042 | Light blue with dark blue flecks | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S042 | Light blue with dark blue flecks
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | Vs001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4060 | 4060 | Y | Office | 099 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | S043 | 2' x 2' fleck
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4062 | 4062 | Y | Office | 100 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 350 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S044 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4063 | 4063 | Y | Office | 101 | Floor | Sheet Flooring | VSF | N | [6 empty] | S045 | Brown stone | [6 empty] | PLEL | Unable to separate mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | S046 | 2' x 4' pinhole fleck
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 4064 | 4064 | Y | Office | 102 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS027 | Blue with dark blue wave | [6 empty] | PLEL | NS as the material was visually similar to S027.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS027 | Blue with dark blue wave | [7 empty] | NS as the material was visually similar to S027.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | S001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4065 | 4065 | Y | Office | 103 | Floor | Sheet Flooring | VSF | P | A | N | SF | 220 | - | - | VS019 | Light green stone | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S019. Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/f
[6 empty] | Mechanical | N/f
[6 empty] | Other | N/F
C | 4066 | 4066 | Y | Office | 104 | Floor | Sheet Flooring | VSF | P | A | N | SF | 220 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material wasv isually similar to S012. Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4044, 4052 | 4044 4052 | Y | Office | 105 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS027 | Blue with dark blue wave | [6 empty] | PLEL | NS as the material was visually similar to S027.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS027 | Blue with dark blue wave | [7 empty] | NS as the material was visually similar to S027.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1024 | 1024 | Y | Office | 106 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S020.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 455 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1027, 1027 A, 1027, B | 1027 | Y | Office | 107 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Plaster | N | [6 empty] | S048 | Plaster
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS046 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S046.
C | 1023, 1023 A | 1023 | Y | Office | 108 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1021, 1021 A | 1021 | Y | Office | 109 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 450 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S049 was collected but not confirmed ACM.S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 6 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 2014 | 2014 | Y | Office | 110 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Wall | Plaster | N | [6 empty] | S050 | Wall plaster
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 5004 A | 5004 | Y | Office | 111 | Floor | Sheet Flooring | VSF | P | A | N | SF | 150 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/f
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 2059 | 2059 | Y | Office | 112 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Ceiling | Stucco | Y | A | N | SF | 40 | - | - | S051 | Stucco | 4 | 0 | 0 | 0 | 0 | 0
C | 2057 | 2057 | Y | Office | 113 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2055 | 2055 | Y | Office | 114 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 2050 | 2050 | Y | Office | 115 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2047 | 2047 | Y | Office | 116 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 2044 | 2044 | Y | Office | 117 | Floor | Tile | Vinyl tile | P | A | N | Sf | 160 | - | - | VS007 | 12' x 12' White with long black streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually the same as S007.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS007 | 12' x 12' White with long black streak | [7 empty] | NS as the material was visually similar to S007
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/f
[6 empty] | Mechanical | N/f
[6 empty] | Other | N/F
C | 2058 | 2058 | Y | Office | 118 | Floor | Tile | Tile mastic | Y | D | N | SF | 700 | - | - | S052 | 12' x 12' Mastic - brown with dark brown and white streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Vinyl tile | N | [6 empty] | S052 | 12' x 12' Brown with dark brown and light browm streaks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 700 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S053 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S054 | 2' x 2' pinhole and large fissure
[6 empty] | Above ceiling |  | Texture | Y | D | N | SF | 350 | - | - | S056 | Texture above ceiling tiles | 2 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | Sink | Tar mastic | Y | D | N | SF | 6 | - | - | S055 | Gold tar on sink | 5 | 0 | 0 | 0 | 0 | 0
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | TRansite | P | A | N | SF | 100 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Countertop | Transite | Y | A | N | SF | 8 | - | - | S057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0
C | 2052 | 2052 | Y | Office | 119 | Floor | Tile | Vinyl tile | Y | A | N | SF | 1344 | - | - | S058 | 12' x 12' Grey with abundant white and brown streaks | 3 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Tile mastic | Y | D | N | SF | 1344 | - | - | S058 | 12' x 12' Grey with abundant white and brown streaks | 5 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | S060 | 2' x 4' pinhole fissure
[6 empty] | Piping | Elbows/Fittings | Parging cement | N | [6 empty] | S059 | Parging cement
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 16 | - | - | VS057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S057.
[6 empty] | Other | Fume Hood | TRansite | P | A | N | SF | 40 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Sink | Tar mastic | P | D | N | SF | 18 | - | - | VS055 | Gold tar on sink | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S055.
C | 2045 | 2045 | Y | Office | 120 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1500 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2039 | 2039 | Y | Office | 121 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | This grey material is new.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new as of 1997.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging cement | NS | [6 empty] | VS059 | Parging cement | [7 empty] | NS as the material was visually similar to S059.
C | 2033 | 2033 | Y | Office | 122 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS045 | Brown stone pattern | [6 empty] | PLEL | NS as the material was visually similar to S045. Unable to separate mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 700 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was visually similar to another sample.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2043 | 2043 | Y | Office | 123 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2029 | 2029 | Y | Office | 124 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Under ceiling panel | Tar paper | N | [6 empty] | S061 | Tar paper
C | 2026 | 2026 | Y | Office | 125 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS025 | Light brown with abundant brown flecks | [6 empty] | PLEL | NS as the material was visually similar to S025.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS025 | Brown with abundant brown flecks | [7 empty] | NS as the material was visually similar to S025.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 2024 | 2024 | Y | Office | 126 | Floor | Sheet Flooring | VSF | N | [6 empty] | S062 | Salmon coloured | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S062 | Salmon coloured
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS034 | 2' x 2' pinhole and hole | [7 empty] | NS as the material is visually similar to S034.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material is visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | A | D | N | EA | 1 | - | VS016 | Tar mastic | [7 empty] | NS as the material is visually similar to S016.
C | 2022 | 2022 | Y | Office | 127 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material is visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2016, 2025, 2025A, 2025B, 2023 | 2016, 2023, 2025 | Y | Office | 128 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Plaster | N | [6 empty] | S063 | Plaster
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [15 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | TRansite | P | A | N | SF | 120 | - | - | VS021 | Transite | 20 | - | - | - | - | - |  | NS as the material was visually similar to S021.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 12 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 2017 | 2017 | Y | Office | 129 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2027 | 2027 | Y | Office | 130 | Floor | Tile | Vinyl tile | P | A | N | SF | 280 | - | - | VS067 | 12' x 12' off white with abundant black streaks | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually the same as S067.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS067 | 12' x 12' off white with abundant black streaks | [7 empty] | NS as the material was visually the same as S067.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS034 | 2' x 2' pinhole and hole | [7 empty] | NS as the material was visually the same as S034.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 2021 | 2021 | Y | Office | 131 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 2001 A-F | 2001 | Y | Office | 132 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2500 | = | - | VS008 | DWjc | 3 | 0 | 0 | 0 | 0 | 0 |  | S064 was collected but not confirmed ACM> S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F | [17 empty] | Limited access above the ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | Limited access above the ceiling.
[6 empty] | Other | Above ceiling tile | Stucco | P | D | N | SF | 180 | - | - | VS051 | Stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S051.
C | 3046 | 3046 | Y | Classroom | 133 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Wall | Plaster | N | [6 empty] | S065 | Wall plaster
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | TRansite | P | A | N | SF | 40 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 10 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 4000 A-D | 4000 | Y | Office | 134 | Floor | Sheet Flooring | VSF | N | [6 empty] | S066 | Cream | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S066 | Cream
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1000 | - | - | VS008 | DWjc | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS046 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S046.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4002 | 4002 | Y | Office | 135 | Floor | Tile | Vinyl tile | Y | A | N | SF | 840 | - | - | S067 | 12' x 12' off white with abundant black streaks | 3 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S067 | 12' x 12' off white with abundant black streaks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 840 | - | - | VS008 | DWjc | 3 | 0 | 0 | 0 | 0 | 0 |  | S069 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S068 | 2' x 4' pinhole and hole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4004 | 4004 | Y | Office | 136 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS068 | 2' x 4' pinhole and hole | [7 empty] | NS as the material was visually the same as S068
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 4006 | 4006 | Y | Office | 137 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS068 | 2' x 4' pinhole and hole | [7 empty] | NS as the material was visually the same as S068
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 4011 | 4011 | Y | Office | 138 | Floor | Tile | Vinyl tile | P | A | N | SF | 840 | - | - | VS067 | 12' x 12' off white with abundant black streaks | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S067.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS067 | 12' x 12' off white with abundant black streaks | [7 empty] | NS as the material was visually similar to S067
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 840 | - | - | VS008 | DWjc | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS068 | 2' x 4' pinhole and hole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4017 | 4017 | Y | Office | 139 | Floor | Tile | Vinyl tile | P | A | N | SF | 840 | - | - | VS067 | 12' x 12' off white with abundant black streaks | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S067.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS067 | 12' x 12' off white with abundant black streaks | [7 empty] | NS as the material was visually similar to S067.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 840 | - | - | VS008 | DWjc | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | VS068 | 2' x 4' pinhole and hole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4017A | 4017 | Y | Office | 140 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS008 | DWjc | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS068 | 2' x 4' pinhole and hole | [7 empty] | NS as the material was visually similar to S068.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4019 | 4019 | Y | Office | 141 | Floor | Tile | Vinyl tile | P | A | N | SF | 600 | - | - | VS067 | 12' x 12' off white with abundant black streaks | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S067.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS067 | 12' x 12' off white with abundant black streaks | [7 empty] | NS as the material was visually similar to S067
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS068 | 2' x 4' pinhole and hole | [7 empty] | NS as the material was visually the same as S068
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4018 | 4018 | Y | Office | 142 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS068 | 2' x 4' pinhole and hole | [7 empty] | NS as the material was visually the same as S068
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4023 | 4023 | Y | Office | 143 | Floor | Tile | Vinyl tile | N | [6 empty] | S070 | 12' x 12' Grey with small white streaks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S070 | 12' x 12' Grey with small white streaks
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually simialr to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4024 A-C, 4022 | 4022, 4024 | Y | Office | 144 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2300 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S072 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS059 | Parging cement | [7 empty] | NS as the material was visually similar to S059.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other |  | Vermiculite | N | [6 empty] | S071 | Vermiculite (lab eqipment)
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 8 | - | - | VS057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S057.
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 180 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 4027 | 4027 | Y | Office | 145 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | [16 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 4028, 4030 | 4028 4030 | Y | Office | 146 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-Bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Tar Mastic | P | A | N | EA | 6 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS059 | Parging cement | [7 empty] | NS as the material was visually similar to S059.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 120 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 56 | - | - | VS057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S057.
C | 4032 | 4032 | Y | Office | 147 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite fume hood | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 8 | - | - | VS057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S057.
C | 4032 A | 4032 | Y | Classroom | 148 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 40 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | N/F
C | 4036 | 4036 | Y | Office | 149 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS036 | Green with wave | [6 empty] | PLEL | NS as the material was visually similar to S036.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS036 | Green with wave | [7 empty] | NS as the material was visually similar to S036.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S073 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-Bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS034 | 2' x 2' pinhole and hole | [7 empty] | NS as the material was visually similar to S034.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Other | Elbows/Fittings | Tar Mastic | P | A | N | EA | 3 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 5001 | 5001 | Y | Classroom | 150 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S074 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS060 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S060.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 220 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | N/F
C | 5002 | 5002 | Y | Classroom | 151 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS060 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S060.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 220 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | N/F
C | 5006 | 5006 | Y | Classroom | 152 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006
[6 empty] | Piping | Sink | Tar | P | D | N | SF | 3 | - | - | VS022 | Tar on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 120 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | N/F
C | 5006 A | 5006 | Y | Office | 153 | Floor | Sheet Flooring | VSF | P | A | N | SF | 140 | - | - | VS019 | Light green stone | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S019. Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Sink | Tar | P | A | N | SF | 2 | - | - | VS022 | Tar under sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 5009 | 5009 | Y | Office | 154 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Fiberglass | NS
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 80 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 24 | - | - | VS057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S057.
C | 5011 | 5011 | Y | Office | 155 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the aterial was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | N/F
C | 5013 | 5013 | Y | Office | 156 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Fiberglass | NS
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 40 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 16 | - | - | VS057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S057.
C | 5016 | 5016 | Y | Office | 157 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 450 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS034 | 2' x 2' pinhole and hole | [7 empty] | NS as the material was visually the same as S034
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visuallysimilar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Sink | Tar | P | A | N | SF | 6 | - | - | VS022 | Tar on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
C | 5023 | 5023 | Y | Office | 158 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS019 | Light green stone | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S019. Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material is visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 5020 | 5020 | Y | Washroom | 159 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 5019 | 5019 | Y | Washroom | 160 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Metal | NS | [15 empty] | NS as metal is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 5017 | 5017 | Y | Office | 161 | Floor | Sheet Flooring | VSF | P | A | N | SF | 400 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS034 | 2' x 2' pinhole and hole | [7 empty] | NS as the material was visually the same as S034.
C | 5015 | 5015 | Y | Office | 162 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S020.
[6 empty] | Floor | Tile | Tile mastic | ns | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 210 | - | - | S075 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
C | 5012 | 5012 | Y | Office | 163 | Floor | Sheet Flooring | VSF | P | A | N | SF | 400 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Sink | Tar | P | D | N | SF | 2 | - | - | VS022 | Tar on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | N/F | [17 empty] | Limited access above the ceiling.
C | 5010 A | 5010 | Y | Office | 164 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS070 | 12' x 12' Grey with small white streaks | [6 empty] | PLEL | NS as the material was visually similar to S070.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS070 | 12' x 12' Grey with small white streaks | [7 empty] | NS as the material was visually similar to S070.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS034 | 2' x 2' pinhole and hole | [7 empty] | NS as the material was visually similar to S034.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 5007 | 5007 | Y | Office | 165 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS025 | Light brown with abundant brown flecks | [6 empty] | PLEL | NS as the material was visually similar to S025.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS025 | Brown with abundant brown flecks | [7 empty] | NS as the material was visually similar to S025.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 120 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS046 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S046.
C | 5022 | 5022 | Y | Office | 166 | Floor | Sheet Flooring | VSF | P | A | N | SF | 256 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 5C01 |  | Y | Office | 167 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the aterial was visually similar to S016.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C |  | 5024 | Y | Office | 168 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually simialr to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4C01 | 4C01 | Y | Office | 169 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 6000 - 6008 | 6000 - 6008 | Y | Office | 170 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF |  |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S078 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | Ea | 91 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Piping | Ends | Parging cement | N | [6 empty] | S079 | Parging cement on ends of borlen
[6 empty] | Piping | Elbows/Fittings | Parging cement | Y | D | N | EA | 1 | - | - | S076 | Parging cement - pipe elbow parging on 6" waterline | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Mechanical | Stacks | Tar mastic | N | [6 empty] | S077 | Tar mastic on stacks
[6 empty] | Other | N/F
C | 4043 A | 4043 | Y | Office | 171 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 4059 | 4059 | Y | Office | 172 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2009 | 2009 | Y | Office | 173 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1034 | 1034 | Y | Office | 174 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling |  | Plaster | NS | [15 empty] | NS as a representative # of samples have been collected.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C |  |  | Y | Office | 175 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
Ceiling
[6 empty] | Piping | Hot water tank | Parging cement | N | [6 empty] | S081 | Parging Cement - pipe elbow parging on liner assor. With DHWT#2
[6 empty] | Mechanical | Boiler | Parging cement | Y | A | Y | SF | 70 | - | - | S080 | Parging cement - on boiler (DHWT #2) | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | N/F
C | 2C04 |  | Y | Corridor | 176 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS046 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S046.
C | 2V04 |  | Y | Corridor | 177 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall |  | Brick & Glass | NS | [15 empty] | NS as these materials are not suspect ACM
[6 empty] | Ceiling | Texture | Stucco | Y | A | N | SF | 400 | - | - | S082 | Ceiling stucco | 4 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2C05 |  | Y | Corridor | 178 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS081 | Parging cement | [7 empty] | NS as the material was visually similar to S081
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually simialr to S009.
C | 2C06 |  | Y | Corridor | 179 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
C | 2C01 |  | Y | Hallway | 180 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Texture | P | A | N | SF | 1440 | - | - | VS082 | Ceiling stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S082
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2C03 |  | Y | Hallway | 181 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinholeq | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging cement | NS | [6 empty] | VS081 | Parging Cement | [7 empty] | NS as the material is visually similar to S081.
C | 2C02 |  | Y | Hallway | 182 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fixed ceiling | Texture | P | A | N | Sf | 75 | - | - | VS082 | Ceiling stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S082
C | 4007 | 4007 | Y | Office | 183 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4008 | 4008 | Y | Office | 184 | Floor | Tile | Vinyl tile | P | A | N | SF | 160 | - | - | VS007 | 12' x 12' White with long black streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S007
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS007 | 12' x 12' White with long black streak | [7 empty] | NS as the material was visually similar to S007
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4010 | 4010 | Y | Office | 185 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4012 | 4012 | Y | Office | 186 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4013 | 4013 | Y | Office | 187 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4014 | 4014 | Y | Office | 188 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4015 | 4015 | Y | Office | 189 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4016 | 4016 | Y | Office | 190 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4020 | 4020 | Y | Office | 191 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4009 | 4009 | Y | Office | 192 | Floor | Tile | Vinyl tile | Y | A | N | SF | 600 | - | - | S083 | 12' x 12' White with black streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S083 | 12' x 12' White with black streak
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4029, 4031 | 4029, 4031 | Y | Office | 193 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2500 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S084 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S085 | 2' x 4' pinhole fleck
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
Other
C | 4034 | 4034 | Y | Office | 194 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 160 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4037 | 4037 | Y | Office | 195 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 140 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS043 | 2' x 2' fleck | [7 empty] | NS as the material was visually the same as S043.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4025, 4025A | 4025 | Y | Office | 196 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4026 | 4026 | Y | Office | 197 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS019 | Green stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S019. Unable to separate mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4039 | 4039 | Y | Office | 198 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4035, 4035A | 4035 | Y | Office | 199 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | [18 empty] | No access above ceiling.
[6 empty] | Mechanical | [18 empty] | No access above ceiling.
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 4038 | 4038 | Y | Office | 200 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
Other
C | 3049 | 3049 | Y | Office | 201 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material is visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Countertop | Transite | P | A | N | Sf | 30 | - | - | VS057 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S057.
C | 3048 | 3048 | Y | Office | 202 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 25 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 3047 | 3047 | Y | Office | 203 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 25 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 3045 | 3045 | Y | Office | 204 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 25 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 3043 | 3043 | Y | Office | 205 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 25 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 3042 | 3042 | Y | Office | 206 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 25 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 3040 | 3040 | Y | Office | 207 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 25 | - | - | VS021 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
C | 3041 | 3041 | Y | Office | 208 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Piping | Sink | Tar | P | D | N | SF | 10 | - | - | VS022 | Tar under sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 3039 | 3039 | Y | Office | 209 | Floor | Sheet Flooring | VSF | NS | [14 empty] | PLEL | New black VSF.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the tile is new.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | Ea | 2 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 3038 | 3038 | Y | Office | 210 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Wall | Plaster | N | [6 empty] | S086 | Wall plaster
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3034 | 3034 | Y | Office | 211 | Floor | Sheet Flooring | VSF | P | A | N | SF | 120 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 6 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 3035 | 3035 | Y | Office | 212 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | Sf | 25 | - | - | VS021 | Transite fume hood | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S021.
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the aterial was visually similar to S016.
C | 3036 | 3036 | Y | Office | 213 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 400 | - | - | S087 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS043 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S043.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the aterial was visually similar to S016.
C | 3033 | 3033 | Y | Office | 214 | Floor | Sheet Flooring | VSF | N | [6 empty] | S088 | Orange VSF | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S088 | Orange VSF
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 3 | - | - | VS016 | tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wasv isually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to S009.
C | 3055 | 3055 | Y | Office | 215 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS052 | 12' x 12' Brown with dark brown and white streaks | [6 empty] | PLEL | NS as the material was visually similar to S052
[6 empty] | Floor | Tile | Tile mastic | P | D | N | SF | 420 | - | - | VS052 | 12' x 12' Brown with dark brown and white streaks | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S052
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 3021 | 3021 | Y | Office | 216 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS089 | 12' x 12' Light grey with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S089
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS089 | 12' x 12' Light grey with black streaks | [7 empty] | NS as the material was visually similar to S089
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS081 | Parging cement | [7 empty] | NS as the material was visually similar to S081.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3019 | 3019 | Y | Office | 217 | Floor | Tile | Vinyl tile | N | [6 empty] | S089 | 12' x 12' Light grey with black streaks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S089 | 12' x 12' Light grey with black streaks
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS081 | Parging cement | [7 empty] | NS as the material was visually similar to S081.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3052 | 3052 | Y | Office | 218 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS046 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as S046.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2013 | 2013 | Y | Office | 219 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Other | N/F
C | 2018 | 2018 | Y | Office | 220 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2019 | 2019 | Y | Office | 221 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2020 | 2020 | Y | Office | 222 | Floor | Sheet Flooring | VSF | P | A | N | SF | 160 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1025, 1025 A, 1026, 1026A | 1025 1026 | Y | Office | 223 | Floor | Sheet Flooring | VSF | NS | [14 empty] | PLEL | NS as the material is new.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 720 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1028 | 1028 | Y | Glass Blowing Shop | 224 | Floor | Sheet Flooring | VSF | P | A | N | SF | - | - | 410 | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Exterior Wall | Tar mastic | P | D | N | SF | 20 | - | - | VS010 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
C | 1030 | 1030 | Y | Welding Shop | 225 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 625 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | - | - | 4 | VS022 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1033 | 1033 | Y | Welding Storage | 226 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1041 | 1041 | Y | Office | 227 | Floor | Sheet Flooring | VSF | P | A | N | SF | 1240 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Texture | N | [6 empty] | S090 | Textured ceiling coat
[6 empty] | Piping | Sink | Tar mastic | P | D | N | Sf | 2- | - | - | VS022 | Tar mastic under sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1041A | 1041 | Y | Office | 228 | Floor | Tile | Vinyl tile | N | [6 empty] | S091 | 12' x 12' Blue with abundant blue and white fleck | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S091 | 12' x 12' Blue with abundant blue and white fleck
[6 empty] | Floor | Sheet Flooring | VSF | P | D | N | Sf | 120 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 |  | Subsurface layer not sampled as it was visually similar to S012.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 1045, 1045A | 1045 | Y | Machine Shop | 229 | Floor | Sheet Flooring | VSF | P | A | N | SF | - | - | 1000 | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS022 | Tar under sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1055 | 1055 | Y | Office | 230 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS045 | Brown VSF | [6 empty] | PLEL | NS as the material was visually similar to S045. Unable to separate mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS | [15 empty] | NS as a representative # of samples have been collected.
[6 empty] | Piping | Sink | Tar | P | D | N | Sf | 2 | - | - | VS022 | Tar under sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S022.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 1017 | 1017 | Y | Office | 231 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 350 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F
C | 1018 | 1018 | Y | Office | 232 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 300 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F
C | 1019 | 1019 | Y | Office | 233 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 1C01 |  | Y | Hallway | 234 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1C03 |  | Y | Hallway | 235 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1C04 |  | Y | Hallway | 236 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as S037
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS061 | Tar paper | [7 empty] | NS as the material was visually similar to S061
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1032 | 1032 | Y | Office | 237 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS039 | 12' x 12' White with abundant brown flecks | [6 empty] | PLEL | NS as the material was visually similar to S039
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS039 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S039
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 1C05 |  | Y | Hallway | 238 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1038 | 1038 | Y | Office | 239 | Floor | Tile | Vinyl tile | N | [6 empty] | S092 | 12' x 12' White with abundant red and blue fleck | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S092 | 12' x 12' White with abundant red and blue fleck
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 330 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS043 | 2' x 2' fleck | [7 empty] | NS as the material was visually similar to S043.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1038A | 1038 | Y | Office | 240 | Floor | Tile | Vinyl tile | N | [6 empty] | S093 | 12' x 12' White with blue fleck | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S093 | 12' x 12' White with blue fleck
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS043 | 2' x 2' fleck | [7 empty] | NS as the material was visually similar to S043.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1C06 |  | Y | Office | 241 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 4 | - | - | VS016 | Tar | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/f
[6 empty] | Other | N/f
C | 1C07 |  | Y | Office | 242 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/f
[6 empty] | Other | N/f
C | 4053 | 4053 | Y | Office | 243 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS019 | Green stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S019. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4C05 |  | Y | Hallway | 244 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4C04 |  | Y | Hallway | 245 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Girders above ceiling | Spray fireproofing | P | D | Y | SF | 400 | - | - | VS038 | Spray fireproofing | 0 | 0 | 0 | 35 | 0 | 0 |  | NS as the material was visually similar to S038.
C | 4C03 |  | Y | Hallway | 246 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | A | N | EA | 1 | - | - | VS016 | tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS061 | Tar paper | [7 empty] | NS as the material was visually similar to S061.
C | 4C02 |  | Y | Hallway | 247 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | A | N | EA | 1 | - | - | VS016 | tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS061 | Tar paper | [7 empty] | NS as the material was visually similar to S061.
C | 4S02 |  | Y | Stairwell | 248 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Texture | Y | A | N | SF | 1600 | - | - | S094 | Stucco | 4 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4S03 |  | Y | Stairwell | 249 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4S02 |  | Y | Stairwell | 250 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4S01 |  | Y | Stairwell | 251 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1016 | 1016 | Y | Office | 252 | Floor | Sheet Flooring | VSF | P | A | N | SF | 2000 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2500 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S096 was collected but not confirmed ACM. S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 10 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually sismilar to S016.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS061 | Tar paper | [7 empty] | NS as the material was visually similar to S061.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS059 | Parging cement | [7 empty] | NS as the material was visually similar to S059.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Exterior Wall | Tar mastic | P | D | N | Sf | 100 | - | - | VS010 | Tar mastic on exterior wall | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
C | 1016 A, 1016 B | 1016 | Y | Office | 253 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4051 | 4051 | Y | Office | 254 | Floor | Sheet Flooring | VSF | P | A | N | SF | 200 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3063 | 3063 | Y | Office | 255 | Floor | Sheet Flooring | VSF | P | A | N | SF | 100 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012. Unable to separate the mastic.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 3065 | 3065 | Y | Office | 256 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1032 | 1032 | Y | Office | 258 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4003 | 4003 | Y | Office | 259 | Floor | Tile | Vinyl tile | P | A | N | SF | 600 | - | - | VS007 | 12' x 12' White with long black streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S007.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS007 | 12' x 12' White with long black streak | [7 empty] | NS as the material was visually similar to S007.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS037 | 2' x 4' pinhole | [7 empty] | NS as the material was visually similar to S037.
[6 empty] | Piping | Elbows/Fittings | Tar paper | NS |  |  | LF | 10 |  |  | VS061 | tar paper | [7 empty] | NS as the material was visually similar to S061.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
C | 5014 | 5014 | Y | Office | 260 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S020.
[6 empty] | Floor | Tile | Tile mastic | ns | [6 empty] | VS020 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 210 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as S006.
C | 1V01 |  | Y | Corridor | 261 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panel | Transite | Y | A | N | SF | 700 | - | - | S097 | Transite panel | 20 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS016 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1035A | 1035 | Y | Office | 262 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1037 | 1037 | Y | Male Washroom | 263 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panels | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1E02 |  | Y | Elevator | 264 | Floor | Tile | Vinyl tile | P | A | N | SF | 100 | - | - | VS007 | 12' x 12' White with long black streak | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S007.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS007 | 12' x 12' White with long black streak | [7 empty] | NS as the material was visually similar to S007.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Ceiling | Panel | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 2054 | 2054 | Y | Office | 265 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panels | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 2053 | 2053 | Y | Office | 266 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Panels | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
C | 3053 | 3053 | Y | Classroon | 268 | Floor | Sheet Flooring | VSF | P | A | N | SF | 600 | - | - | VS012 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S012.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to S001.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 1054 | 1054 | Y | Classroon |  | Floor | Sheet Flooring | VSF | P | A | N | SF | 165 | - | - | VS12 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present in sample VS12
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS34 | 2"X2" pinhole and hole | [7 empty] | No ACM present in sample VS34
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete | NS | [15 empty] | NS as material is not suspect ACM.
C | 1054A | 1054 | Y | Classroon |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS34 | 2"X2" pinhole and hole | [7 empty] | No ACM present in sample VS34
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete | NS | [15 empty] | not insulated
C | 1047 | 1047 | Y | Classroon |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 1001 | 1001 | Y | Classroon |  | Floor | Tile | Vinyl tiles | NS | [6 empty] | VS005 | 12"x12" vinyl floor tiles, grey with black streak | [6 empty] | PLEL | No ACM present in sample VS05
[6 empty] | Wall | Fixed | Plaster | NS
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS34 | 2"x2" acoustic ceiling tile, pinhole and hole pattern | [7 empty] | No ACM present in sample VS34
[6 empty] | Piping | Elbows/Fittings | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete | [16 empty] | Structure is not insulated
C | 2012 | 2012 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [7 empty] | new sheet flooring | [6 empty] | PLEL | No ACM present as VSF is new.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 3400 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in VS08
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | 2"x2" Acoustic Ceiling Tile (NEW) | [7 empty] | No ACM present as ACT is new
[6 empty] | Piping | Elbows/Fittings | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete | [16 empty] | Structure is not insulated
C | 2012A | 2012 | Y |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in VS08
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | 2"x2" Acoustic Ceiling Tile (NEW) | [7 empty] | No ACM present as ACT is new
[6 empty] | Piping | Elbows/Fittings | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete | [16 empty] | Structure is not insulated
C | 2012B, C, D | 2012 | Y | Meeting Room, Lunch Room |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in VS08
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | 2"x2" Acoustic Ceiling Tile (NEW) | [7 empty] | No ACM present as ACT is new
[6 empty] | Piping | Elbows/Fittings | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete | [16 empty] | Structure is not insulated
C | 2008 | 2008 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [14 empty] | PLEL | No ACM present as VSF is new.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1450 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in VS08
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 730 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in VS08
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 2008A | 2008 | Y | Cold Storage |  | Floor | Steel | Steel | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Steel | Steel | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Steel | Steel | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 2008B | 2008 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [14 empty] | PLEL | No ACM present as VSF is new.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 340 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in VS08
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"x2" acoustic ceiling tile, pinhole and fleck | [7 empty] | No ACM present as Sample is VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete
C | 1069 | 1069 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Straight run | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete | Concrete | NS | [15 empty] | not insulated; NS as concrete is not suspect ACM.
C | 2008C | 2008 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in drywall as sample is VS08
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 150 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as in drywall as sample is VS08
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 3054B | 3054 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS | [6 empty] | VS86 | plaster | [7 empty] | No ACM present as sample is VS86.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 3061A | 3061 | Y |  |  | Floor | Sheet Flooring | VSF | P | A | N | SF | 150 |  |  | VS12 | vinyl sheet flooring, cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present as sample VS12
[6 empty] | Wall | concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"x2" acoustic ceiling tile, pinhole and fleck | [7 empty] | No ACM present as sample is VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 4048 | 4048 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS34 | 2"x2" acoustic ceiling tile, pinhole and hole | [7 empty] | No ACM present as sample is VS34
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 4017B | 4017 | Y |  |  | Floor | Tile | Vinyl tiles | P | A | N | SF | 75 |  |  | VS007 | 12"X12" VINYL FLOOR TILES, WHITE WITH BLACK STREAK | 3 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present as sample VS07
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 240 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample is VS08
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS37 | 2"X4" acoustic ceiling tile, pinhole pattern | [7 empty] | No ACM present as sample is VS37
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | not insulated
[6 empty] | Structure | N/F
C | 1008 | 1008 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging cement | N | [6 empty] | S99 | parging cement on elbow associated with DHWT-2
[6 empty] | Mechanical | Tank | Insulation | Y | C | Y | SF | 116 | 4 |  | S98 | Parging cement and magblock; insulated tank DHWT'S-2 | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Structure | Concrete | Concrete | NS
C | 1012 | 1012 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | Elbows/Fittings | Tar paper | NS | [6 empty] | VS61 | tar paper covering fiberglass above ceiling | [7 empty] | no acm as sample is VS61
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Structure | Concrete | Tar mastic |  |  |  | % | 100 |  |  | S100 | tar mastic on foam structured insulation | 15 | 0 | 0 | 0 | 0 | 0 |  | Sample results for S100??
C | 1011 | 10011 | Y |  |  | Floor | Sheet Flooring | VSF | P |  | N | SF | 160 |  |  | VS12 | vinyl sheet flooring, cream colored stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present as sample VS12
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | N/F | [17 empty] | not insulated
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete | Concrete | NS | [15 empty] | not insulated
C | 1013-F | 1013 | Y | Bathroom |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | no acm as sample is VS01
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS59 | pipe elbow parging - 4 elbows | [7 empty] | no acm as sample is VS59
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Structure | Concrete | Concrete | NS | [15 empty] | not insulated; NS as concrete is not suspect ACM.
C | 1014 | 1014 | Y |  |  | Floor | Tile | Vinyl tiles | NS | [6 empty] | VS89 | 12"x2" vinyl floor tiles, light grey with black streak | [6 empty] | PLEL | no acm as sample is VS89
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | no acm as sample is VS01
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS59 | pipe elbow parging - 2 elbows | [7 empty] | no acm as sample is VS59
[6 empty] | Piping | Elbows/Fittings | Tar paper | NS | [6 empty] | VS61 | tar paper covering fiberglass insulation above ceiling | [7 empty] | no acm a sample is VS61
[6 empty] | Structure | Concrete | Concrete | NS | [15 empty] | not insulated
C | 1015 | 1015 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | Elbows, no fittings | Tar paper | NS | [6 empty] | VS61 | tar paper covering fiberglass above ceiling | [7 empty] | no acm as sample is VS61
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Structure | Concrete | Concrete | NS |  |  | % | 100 |  |  | VS100 | tar mastic on foam structured insulation | 15 | 0 | 0 | 0 | 0 | 0 |  | not insulated
C | 1017A | 1017 | Y |  |  | Floor | Concrete |  | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Concrete/wood | Concrete/wood | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS | [6 empty] | VS86 | plaster | [7 empty] | No ACM present as sample is VS86.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 1018A | 1018 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS | [6 empty] | VS86 | plaster | [7 empty] | No ACM present as sample is VS86.
[6 empty] | Piping | Straight run |  | NS | [15 empty] | not insulated
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F
C | 1020 | 1020 | Y |  |  | Floor | Tile | Vinyl tiles | NS | [6 empty] | VS91 | 12"x12" vinyl floor tiles, blue with abundant blue and white flecks | [6 empty] | PLEL | No acm as sample is VS91
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1000 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample VS08
[6 empty] | Wall | Wood | Wood | NS
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS46 | 2"x4" acoustic ceiling tile, pinhole and fleck pattern | [7 empty] | No ACM present as sample is VS46
[6 empty] | Piping | N/F | [17 empty] | no access above ceiling (room restrictions)
[6 empty] | Mechanical | N/F | [17 empty] | no access above ceiling (room restrictions)
[6 empty] | Other | N/F | [17 empty] | no access above ceiling (room restrictions)
C | 1020A | 1020 | Y |  |  | Floor | Tile | Vinyl tiles | NS | [6 empty] | VS91 | 12"x12" vinyl floor tiles, blue with abundant blue and white flecks | [6 empty] | PLEL | No acm as sample is VS91
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1000 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample VS08
[6 empty] | Wall | Wood | Wood | NS
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS46 | 2"x4" acoustic ceiling tile, pinhole and fleck pattern | [7 empty] | No ACM present as sample is VS46
[6 empty] | Piping | N/F | [17 empty] | no access above ceiling (room restrictions)
[6 empty] | Mechanical | N/F | [17 empty] | no access above ceiling (room restrictions)
[6 empty] | Other | N/F | [17 empty] | no access above ceiling (room restrictions)
C | 1022 | 1022 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" ACT pinhole pattern | [7 empty] | No ACM present as sample is VS01
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS59 | pipe elbow parging | [7 empty] | no acm present as sample is VS59
[6 empty] | Piping | tar paper | Tar paper | NS | [6 empty] | VS61 | tar paper covering insulation above ceiling | [7 empty] | no acm present as sample is VS61
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
C | 1022A | 1022 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" ACT pinhole pattern | [7 empty] | No ACM present as sample is VS01
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS59 | pipe elbow parging | [7 empty] | no acm present as sample is VS59
[6 empty] | Piping | tar paper | Tar paper | NS | [6 empty] | VS61 | tar paper covering insulation above ceiling | [7 empty] | no acm present as sample is VS61
[6 empty] | Other | Concrete | Tar mastic | P | C | N | SF | 210 |  |  | VS100 | tar mastic on foam structured insulation | 15 | 0 | 0 | 0 | 0 | 0 |  | acm present as sample VS100
C | 1031 | 1031 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS | [6 empty] | VS86 | plaster | [7 empty] | No ACM present as sample is VS86.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS99 | parging cement | [7 empty] | no acm present as sample is VS99
[6 empty] | Mechanical | tank | Insulation | P | C | Y | SF | 150 |  |  | VS98 | tank insulation | 30 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample is VS98
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 1032B | 1032 | Y | Storage |  | Floor | Carpet |  | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 1032C | 1032 | Y |  |  | Floor | Concrete |  | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | No ceiling | [17 empty] | no ceiling
[6 empty] | Piping | Straight run |  | NS | [15 empty] | not insulated
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Structure | Concrete |  | NS
C | 1034 | 1034 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | 0 | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 280 |  |  | VS008 | Drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | acm present as sample VS08
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 140 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | acm present as sample VS08
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 1034A | 1034 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 1034B | 1034 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS59 | pipe elbow parging - 2 fittings | [7 empty] | no acm found as sample is VS59
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Structure | Concrete | Fiberglass | NS | [7 empty] | insulation
C | 1036 | 1036 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | Elbows/Fittings | Fiberglass | NS | [7 empty] | 2 fittings - fiberglass | [7 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated; NS as concrete is not suspect ACM.
C | 2031A | 2031 | Y |  |  | Floor | Sheet Flooring | VSF | P | A | N | SF | 131 |  |  | VS12 | vinyl sheet flooring, cream colored stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present as sample is VS12
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 2031B | 2031 B | Y | Storage |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 45 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | no acm present as sample is VS08
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 2042 | 2042 | Y | Mechanical Room |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 320 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample is VS08
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS54 | 2"x2" acoustic ceiling tile, pinhole and large fissure | [7 empty] | no acm present as sample is VS54
[6 empty] | Piping | Straight run | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated; NS as concrete is not suspect ACM.
C | 2043A | 2043 | Y | Data Closet |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | wood/concrete | wood/concrete | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 2055 | 2055 | Y |  |  | Floor | Carpet |  | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Concrete |  | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Steel | Steel | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 2060 | 2060 | Y | Storage |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete |  | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Textured ceiling | Texture | P | C | N | SF | 172 |  |  | VS56 | textured ceiling coat above ceiling | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as sample is similat to S56
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 2004 | 2004 | Y |  |  | Floor | Sheet Flooring | rubber | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 5890 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | acm is present as sample is VS08
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"x2" acoustic ceiling tile, pinhole with fleck patterm | [7 empty] | no acm present as sample is VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated; NS as concrete is not suspect ACM.
C | 2004A | 2004 | Y | Office |  | Floor | Sheet Flooring | rubber | NS | [14 empty] | PLEL
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 430 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | acm is present as sample is VS08
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"x2" acoustic ceiling tile, pinhole with fleck patterm | [7 empty] | no acm present as sample is VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 2010 | 2010 | Y | Office |  | Floor | Sheet Flooring | rubber | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 3200 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | acm is present as sample is VS08
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"x2" acoustic ceiling tile, pinhole with fleck patterm | [7 empty] | no acm present as sample is VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 2003 | 2003 | Y |  |  | Floor | Carpet |  | NS | [14 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 5678 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | acm is present as sample is VS08
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"x2" acoustic ceiling tile, pinhole with fleck patterm | [7 empty] | no acm present as sample is VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | this room was surveyed from the door - could not get into room.
C | 2002-A | 2002 | Y | Bathroom |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete |  | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | no access above ceiling
C | 2002 | 2002 | Y | Corridor |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete |  | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Textured ceiling | Texture | P | C | N | SF | 120 |  |  | VS56 | textured ceiling coat above ceiling | 2 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample is VS56
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | no access above ceiling
C | 1067 | 1067 | Y |  |  | Floor | Tile | Terrazzo | NS | [15 empty] | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Fixed | Plaster | NS | [6 empty] | VS28 | Wall plaster | [7 empty] | NS as sample was similar to S28
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"x2" acoustic ceiling tile, pinhole and fleck pattern | [7 empty] | no acm present as sample was VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | NO ACCESS ABOVE CEILING, TOO HIGH.
C | 1065 | 1065 | Y |  |  | Floor | Tile | Terrazzo | NS | [15 empty] | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete |  | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete |  | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | no access above ceiling.
C | 1062A | 1062 | Y | Office |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Fixed | Plaster | NS | [6 empty] | VS13 | Plaster under window | [7 empty] | NS as the material was visually similar to VS13.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | Sink | Black tar | Y | A | N | SF | 2 | - | 2 | VS22 | Tar under sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as material is similar to S22
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | Y | A | N | SF | 30 | - | - | VS21 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as material issimilar to S21
C | 1055A | 1055 | Y | Mechanical Room |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample is VS08
[6 empty] | Wall | Concrete | Concrete
[6 empty] | Ceiling | Fixed | Plaster | NS | [7 empty] | ceiling plaster
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 1053A | 1053 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | no acm present as sample is VS01
[6 empty] | Piping | Straight run | Fiberglass | NS
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete | [17 empty] | no acm present as sample is VS99
C | 5016A | 5016 | Y | Office | 157 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 450 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS08 of DWJC was ACM; therefore all DWJC is consider ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS34 | 2' x 2' pinhole and hole | [7 empty] | NS as the material was visually the same as VS34
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visuallysimilar to VS09.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Sink | Tar | P | A | N | SF | 6 | - | - | VS22 | Tar on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS22.
C | 4020A | 4020 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete/Wood | Concrete/Wood | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" pinhole pattern | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling
C | 4020B | 4020 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete/Wood | Concrete/Wood | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" pinhole pattern | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling
C | 4017A | 4017 | Y | Office | 140 | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS08 of DWJC was ACM; therefore all DWJC is consider ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS68 | 2' x 4' pinhole and hole | [7 empty] | NS as the material was visually similar to VS68.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 4005 | 4005 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 4001 | 4001 | Y |  |  | Floor | Sheet Flooring | rubber | NS | [7 empty] | rubber sheet flooring | [6 empty] | PLEL | NS as material is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2"X2" ACOUSTIC CEILING TILE, PINHOLE WITH FLECK PATTERN | [7 empty] | NF as sample is visually the same as VS06
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 1052,1052A | 1052 | Y | Office | 018 | Floor | Sheet Flooring | VSF | P | A | N | SF | 1200 | - | - | VS12 | Cream stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to VS12. Unable to separate the mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Wall | Column | Texture | P | A | Y | SF | 20 | - | - | VS14 | Decorative coating/texture on column | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS14.
[6 empty] | Wall | Exterior Wall | Tar mastic | P | D | N | SF | 300 | - | - | VS10 | Tar mastic | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS10.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 1 | - | - | VS16 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS16.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to VS09.
C | 4046 | 4046 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS27 | Blue with dark blue wave | [6 empty] | PLEL | NS as the material was visually similar to VS27.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS27 | Blue with dark blue wave | [7 empty] | NS as the material was visually similar to VS27.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4046A | 4046 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS27 | Blue with dark blue wave | [6 empty] | PLEL | NS as the material was visually similar to VS27.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS27 | Blue with dark blue wave | [7 empty] | NS as the material was visually similar to VS27.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4050 | 4050 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS27 | Blue with dark blue wave | [6 empty] | PLEL | NS as the material was visually similar to VS27.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS27 | Blue with dark blue wave | [7 empty] | NS as the material was visually similar to VS27.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4030A | 4030 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | A | N | EA | 6 | - | - | VS16 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS16.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS59 | Parging cement | [7 empty] | NS as the material was visually similar to VS59.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 120 | - | - | VS21 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS21.
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 56 | - | - | VS57 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS57.
C | 4028A | 4028 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | A | N | EA | 6 | - | - | VS16 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS16.
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS | [6 empty] | VS59 | Parging cement | [7 empty] | NS as the material was visually similar to VS59.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 120 | - | - | VS21 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS21.
[6 empty] | Other | Countertop | Transite | P | A | N | SF | 56 | - | - | VS57 | Transite countertop | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS57.
C | 4021 | 4021 | Y |  |  | Floor | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Fixed | Plaster | NS | [6 empty] | VS86 | plaster on wall | [7 empty] | Sample VS86
[6 empty] | Ceiling | Fixed | Plaster | NS | [15 empty] | NS as material is similar to S86
[6 empty] | Piping | Elbows/Fittings | Parging cement | NS |  |  |  | 2 elbows |  |  | VS59 | Parging cement | [7 empty] | NS as the material was visually similar to VS59.
[6 empty] | Mechanical | N/F
[6 empty] | Structure | N/F
[6 empty] | Other | N/F
C | 1048-1049 | 1048-49 (joined rooms) | Y |  |  | Floor | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM
[6 empty] | Ceiling | Fixed | Plaster | NS
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
[6 empty] | Other | N/F
C | 1050A | 1050 | Y |  |  | Floor | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM
[6 empty] | Ceiling | Fixed | Plaster | NS
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
[6 empty] | Other | N/F
C | 3052A | 3052 | Y | Office | 218 | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS46 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually the same as VS46.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4057A/B/C | 4057 | Y | Office | 096 | Floor | Sheet Flooring | VSF | N | [6 empty] | VS41 | Cream VSF | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | VS41 | Cream VSF
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F | [17 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | N/F | [17 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 5018 | 5018 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 120 |  |  | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS78 was collected but not confirmed ACM. VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 91 | - | - | VS16 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS16.
[6 empty] | Piping | Ends | Parging cement | NS | [6 empty] | VS79 | Parging cement on ends | [7 empty] | NS as material is similer to S79
[6 empty] | Piping | Water lines | Parging cement | P | D | N | EA | 1 | - | - | VS76 | Parging cement on 6" water line | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as material is similer to S79
[6 empty] | Mechanical | Stacks | Tar mastic | NS | [6 empty] | VS77 | Tar mastic on stacks | [7 empty] | NS as material is similer to S77
[6 empty] | Other | N/F
C | 5010 | 5010 | Y |  |  | Floor | Sheet Flooring | VSF | P | A | N | SF | 2300 |  |  | VS12 | vinyl sheet flooring, cream colored stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present as sample VS12
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | VS78 was collected but not confirmed ACM. VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | No ACM as sample VS01
[6 empty] | Piping | Elbows/Fittings | Fiberglass | NS | [7 empty] | straight run
[6 empty] | Mechanical | Ductwork | Fiberglass | NS
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 5021 | 5021 | Y |  |  | Floor | Tile | Terrazzo | NS | [15 empty] | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete |  | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | Straight Run | Fiberglass | NS
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 5024 | 5024 | Y |  |  | Floor | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 480 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | VS74 was collected but not confirmed ACM. VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Wall | Concrete | Concrete | NS
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 6002-A | 6002 | Y |  |  | Floor | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Fiberglass |  | NS
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 5001A,B | 5001 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 2400 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS74 was collected but not confirmed ACM. VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS37 | 2' x 4' pinhole | [7 empty] | NS as the material was visually the same as VS37
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS60 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to VS60.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to VS09.
[6 empty] | Mechanical | Fume Hood | Transite | P | A | N | SF | 220 | - | - | VS21 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS21.
[6 empty] | Other | N/F
C | 5004 | 5004 | Y |  |  | Floor | Sheet Flooring | VSF | P | A | N | SF | 340 |  |  | VS12 | vinyl sheet flooring, cream colored stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present as sample is VS12
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | NS as sample is VS01
[6 empty] | Piping | Straight Run
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | N/F | [17 empty] | not insulated
C | 4044A | 4044 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS27 | Blue with dark blue wave | [6 empty] | PLEL | NS as the material was visually similar to VS27.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS27 | Blue with dark blue wave | [7 empty] | NS as the material was visually similar to VS27.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 4042A | 4042 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Fixed | Plaster | NS | [6 empty] | VS86 | WALL PLASTER | [7 empty] | NS as sample is VS86
[6 empty] | Ceiling | Fixed | Plaster | NS | [6 empty] | VS86 | WALL PLASTER | [7 empty] | Note: 6 ft2 of plaster debris
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | [18 empty] | No access above ceiling
C | 3050 | 3050 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Fixed | Plaster | NS | [6 empty] | VS86 | WALL PLASTER | [7 empty] | NS as material is similar to S86
[6 empty] | Ceiling | acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" Pinhole pattern | [7 empty] | NS as sample is VS01
[6 empty] | Piping | N/F | [17 empty] | not insulated
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated; NS as concrete is not suspect ACM.
C | 4040 | 4040 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Fixed | Plaster | NS | [6 empty] | VS86 | WALL PLASTER | [7 empty] | NS as material is similar to S86
[6 empty] | Ceiling | acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" Pinhole | [7 empty] | NS as sample is VS01
[6 empty] | Piping | N/F | [17 empty] | not insulated
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated; NS as concrete is not suspect ACM.
C | 3054 | 3054 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS36 | Green with wave | [6 empty] | PLEL | NS as the material was visually similar to VS36.
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS36 | Green with wave | [7 empty] | NS as the material was visually similar to VS36.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | Sink | Tar mastic | P | D | N | SF | 2 | - | - | VS22 | Tar mastic on sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS22.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
C | 2033A | 2033 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling because of smoke alarm.
C | 3056 | 3056 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling because of smoke alarm.
C | 3066 | 3066 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling because of smoke alarm.
C | 3E03,4E01,4E02,4E03 | 3 E03, 4E01-03 | Y |  |  | Floor | Tile | Vinyl tiles | NS |  |  | SF |  |  |  | VS11 | 12"x12" white with black streak vinyl floor tiles | [6 empty] | PLEL | NS as sample is VS11
[6 empty] | Wall | Steel | Steel | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Ceiling | steel | Steel | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling.
C | 4054 | 40 54 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as sample VS08
[6 empty] | Wall | Concrete | Concrete | NS
[6 empty] | Ceiling | Fixed | Plaster | NS
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling.
C | 1043 | 10 43 | Y | Storage |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Other | Concrete |  | NS | [15 empty] | not insulated
C | 2030 | 20 30 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS | [15 empty] | NF as sample is VS59
[6 empty] | Piping | Straight Run | Parging cement | NS | [6 empty] | VS59 | pipe elbow parging and fiberglass | [7 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | N/F | [17 empty] | not insulated
[6 empty] | Structure |  |  | NS | [15 empty] | no access above ceiling
C | 2E02(elevator),5E01 | 2 E02, 5E01 | Y | Elevator |  | Floor | rubber | rubber | NS | [14 empty] | PLEL
[6 empty] | Wall | Steel | Steel | NS
[6 empty] | Ceiling | Steel | Steel | NS
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure |  |  | NS | [15 empty] | no access above ceiling
C | 3037 | 30 37 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"X2" pinhole | [7 empty] | NF as sample was VS01
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as material is not suspect ACM.
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure |  |  | NS | [15 empty] | no access above ceiling
C | 3032 | 30 32 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL
[6 empty] | Wall | Fixed | Plaster | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | NS |  |  | SF
[6 empty] | Piping | Straight Run | Fiberglass | NS
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure |  |  | NS | [15 empty] | no access above ceiling
C | 4063A | 4063 | Y | Office | 101 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS45 | Brown stone | [6 empty] | PLEL | Unable to separate mastic.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS46 | 2' x 4' pinhole fleck
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
C | 4061 | 4061 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as VS01.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | [18 empty] | No access above ceiling because of smoke alarm.
C | 3020A | 3020 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Fixed | Plaster
[6 empty] | Wall | Concrete | Concrete | NS
[6 empty] | Ceiling | Fixed | plaster/drywall | P | A | N | SF | 400 |  |  | VS008 | drywall joint compound | 3 | 0 | 0 | 0 | 0 | 0 |  | ACM present as dwjc is VS08
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Structure | Concrete |  | NS | [15 empty] | No access above ceiling because of smoke alarm.
C | 3013 | 3013 | Y |  |  | Floor | Sheet Flooring | VSF | P | A | N | SF | 142 |  |  | VS12 | vinyl sheet flooring, cream colored stone pattern | 15 | 0 | 0 | 0 | 0 | 0 | PLEL | ACM present as sample VS12
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | N/F | [17 empty] | not insulated
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 3009 | 3009 | Y |  |  | Floor | Tile | Terrazzo | NS | [14 empty] | PLEL | NS as terrazzo is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2"x2" acoustic ceiling tile, pinhole pattern | 0 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS01.
[6 empty] | Piping | N/F | [17 empty] | not insulated
[6 empty] | Mechanical | Ductwork |  | NS | [15 empty] | not insulated
[6 empty] | Structure | Concrete |  | NS | [15 empty] | not insulated
C | 3005F | 3005 | Y |  |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS25 | Light brown with brown fleck | [6 empty] | PLEL | NS as the material was visually similar to VS25.
[6 empty] | Floor | Sheet Flooring | VSF mastic | NS | [6 empty] | VS25 | Light brown with brown fleck | [7 empty] | NS as the material was visually similar to VS25.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 120 | - | - | VS008 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | VS08 of DWJC was ACM; therefore all DWJC is considerC ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS006 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually the same as VS06.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
C | 3041A,3041B | 3041 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 2' pinhole | [7 empty] | NS as the material was visually similar to VS01.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | P | D | N | EA | 2 | - | - | VS16 | Tar mastic | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS16.
[6 empty] | Piping | Sink | Tar | P | D | N | SF | 10 | - | - | VS22 | Tar under sink | 10 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to VS22.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS009 | Tar paper | [7 empty] | NS as the material was visually similar to VS09.