## Sheet1
Building | Room # | Room # (numeric) | Room Accessed (Y/N) | Location Description | PLEL Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[12 empty] | Unit of Measure | Condition
[13 empty] | Good | Fair | Poor
AX | 1001 | 1001 | Y | Main Boiler Room | 001 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | N | [6 empty] | S003 | Parging Cement on 6" Waterlines
[6 empty] | Piping | Elbows/Fittings | Parging Cement | Y | D | Y | EA | 8 | - | - | S004 | Parging Cement on 4" Waterlines | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | Elbows/Fittings | Parging Cement | Y | D | Y | EA | 22 | - | - | S005 | Parging Cement on 6" Waterlines | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Mechanical | Steam Header | Insulation | Y | A | Y | SF | 60 | - | - | S001 | Insulation on steam header | 10 | 0 | 0 | 15 | 0 | 0
[6 empty] | Mechanical | Boiler Exhaust | Insulation | Y | A | Y | SF | 210 | - | - | S002 | Insulation on boiler exhaust | 40 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | Boiler | Textile Gasket | N | [6 empty] | S006 | Textile Gasket on boilers 1 and 2
AX | 1000B | 1000 | Y | Office | 002 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 1000 | 1000 | Y | Condenser Room | 003 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement on Waterlines | [7 empty] | NS as the material was visually similar to S003.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 22 | - | - | VS005 | Parging Cement on Waterlines | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | Tank | Insulation | Y | A | Y | SF | 92 | - | - | S007 | Tank Insulation | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | N/F
AX |  |  | Y | Utilities Tunnel (no room #) | 004 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement on Waterlines | [7 empty] | NS as the material was visually similar to S003.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 8 | - | - | VS004 | Parging Cement on Waterlines | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 2005A | 2005 | Y | Office | 005 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S008 was collected but not confirmed ACM. S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 2004 | 2004 | Y | Office | 006 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 2005 | 2005 | Y | Office | 007 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 2002 | 2002 | Y | Office | 008 | Floor | Tile | Vinyl tile | N | [6 empty] | S009 | 12' x 12' White with brown streaks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S009 | 12' x 12' White with brown streaks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 2C01 |  | Y | Hallway | 009 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 2S02 |  | Y | Stairwell | 010 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Above Ceiling | Tar | N | [6 empty] | S010 | Tar roof material
AX | 2003 | 2003 | Y | Washroom | 011 | Floor | Tile | Vinyl tile | N | [6 empty] | S011 | 12' x 12' White with abundant brown flecks | [6 empty] | PLEL
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 60 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was collected but not confirmed ACM. S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 60 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 2001B | 2001 | Y | Technical Services | 012 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Fume Hood | Transite | Y | A | N | SF | 14 | - | 1 | S013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 2V01 |  | Y | Entrance to Elevarir | 013 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 2000A | 2000 | Y | Office | 014 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 2000 | 2000 | Y | Lab | 015 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 2V02 |  | Y | Entrance | 016 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 2S02 |  | Y | Stairwell | 017 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S014 | 2' x 4' pinhole fissure
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | 1 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S004.
AX | 3C01 |  | Y | Hallway | 018 | Floor | Tile | Vinyl tile | N | [6 empty] | S015 | 12' x 12' Beige with brown streaks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S015 | 12' x 12' Beige with brown streaks
[6 empty] | Floor | Tile | Vinyl tile | Y | A | N | SF | 460 | - | - | S016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 |  | No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 515 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S018 was collected but not confirmed ACM. S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | S017 | 2' x 4' pinhole fleck
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 8 | - | - | VS004 | PArging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S004.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 3001 | 3001 | Y | Office | 019 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | Sf | 20 | - | - | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
AX | 3001B | 3001 | Y | Office | 020 | Floor | Tile | Vinyl tile | N | [6 empty] | S019 | 12' x 12' Grey | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S019 | 12' x 12' Grey
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S007 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 3000 | 3000 | Y | Office | 021 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 3000A | 3000 | Y | Wet Lab | 022 | Floor | Tile | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F | [17 empty] | No acces above the ceiling.
[6 empty] | Other | N/F
AX | 3002A | 3002 | Y | Office | 023 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 3004 | 3004 | Y | Office | 024 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS019 | 12' x 12' Grey | [6 empty] | PLEL | NS as the material was visually siimlar to S019
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS019 | 12' x 12' Grey | [7 empty] | NS as the material was visually similar to S019.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S007 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 3005 | 3005 | Y | Office | 025 | Floor | Tile | Vinyl tile | P | A | N | Sf | 450 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S016. No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 450 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S007 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 9 | - | - | VS004 | Parging Cement | 30 | - | - | - | - | - |  | NS as the material was visually similar to S004.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | SF | 20 | - | - | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
AX | 3006 | 3006 | Y | Male Washroom | 026 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 3008 | 3008 | Y | Female Washroom | 027 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 2S01 |  | Y | Stairwell | 028 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | 1 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S004.
AX | 4C01 |  | Y | Hallway | 029 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS015 | 12' x 12' Beige with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S015
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS015 | 12' x 12' Beige with brown streaks | [7 empty] | NS as the material was visually similar to S015
[6 empty] | Floor | Tile | Vinyl tile | P | A | N | Sf | 1500 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S016
[6 empty] | Wall | Drywall | DWJC | Y | A | N | Sf | 1630 | - | - | S020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AX | 4000 | 4000 | Y | Office | 030 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS019 | 12' x 12' Grey | [6 empty] | PLEL | NS as the material was visually similar to S019.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS019 | 12' x 12' Grey | [7 empty] | NS as the material was visually similar to S019.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 70 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AX | 4001 | 4001 | Y | Office | 031 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 200 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AX | 4003 | 4003 | Y | Office | 032 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS019 | 12' x 12' Grey | [6 empty] | PLEL | NS as the material was visually similar to S019.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS019 | 12' x 12' Grey | [7 empty] | NS as the material was visually similar to S019.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 150 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AX | 4007 | 4007 | Y | Office | 033 | Floor | Tile | Vinyl tile | P | A | N | Sf | 150 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S016. No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 150 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AX | 4012 | 4012 | Y | Office | 034 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 150 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AX | 4010 | 4010 | Y | Office | 035 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 150 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS014 | 2' x 4' pinhole fissure | [7 empty] | NS as the material was visually similar to S014.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
AX | 4013 | 4013 | Y | Office | 036 | Floor | Tile | Vinyl tile | N | [6 empty] | S021 | 12' x 12' White with blue flecks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S021 | 12' x 12' White with blue flecks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS017 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No acces above the ceiling.
AX | 4016 | 4016 | Y | Office | 037 | Floor | Tile | Vinyl tile | P | A | N | Sf | 670 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S016. No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 670 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS017 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | p | A | N | SF | 100 | = | = | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
AX | 4015 | 4015 | Y | Office | 038 | Floor | Tile | Vinyl tile | P | A | N | Sf | 350 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S016. No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 350 | - | - | S022 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS017 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | p | A | N | SF | 50 | = | = | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
AX | 4011 | 4011 | Y | Office | 039 | Floor | Tile | Vinyl tile | P | A | N | Sf | 400 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S016. No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS017 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | p | A | N | SF | 60 | = | = | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
AX | 4009 | 4009 | Y | Cold Room | 040 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 4005 | 4005 | Y | Office | 041 | Floor | Tile | Vinyl tile | P | A | N | Sf | 400 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S016. No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS017 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | p | A | N | SF | 60 | = | = | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
AX | 4002 | 4002 | Y | Office | 042 | Floor | Tile | Vinyl tile | P | A | N | Sf | 400 | - | - | VS016 | 12' x 12' Beige with thick brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S016. No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS017 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | p | A | N | SF | 60 | = | = | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
OS |  |  | Y | Overpass to OSC (no room #) | 043 | Floor | Tile | Vinyl tile | NS | [6 empty] | VS009 | 12' x 12' White with brown streaks | [6 empty] | PLEL | NS as the material was visually similar to S009.
[6 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS009 | 12' x 12' White with brown streaks | [7 empty] | NS as the material was visually similar to S009.
[6 empty] | Wall |  | Glass | NS | [15 empty] | NS as glass is not suspect ACM.
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 1 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 5000 | 5000 | Y | Phycosium | 044 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 34 | 0 | 0 | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4000A | 4000 | Y | Office | 045 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 7 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4001, 4000 | 4000 4001 | Y | Office | 046 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 13 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4003 | 4003 | Y | Office | 047 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 9 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | Sf | 40 | - | - | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013.
OS | 4005 | 4005 | Y | Office | 048 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 4 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4007A | 4007 | Y | Office | 049 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4008 | 4008 | Y | Office | 050 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 9 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4009, 4010 | 4009 4010 | Y | Office | 051 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 13 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | 7 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S005
OS | 4010A | 4010 | Y | Office | 052 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 7 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4012 | 4012 | Y | Office | 053 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 2 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | 6 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S005
OS | 4016 | 4016 | Y | Office | 054 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 4 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | 3 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S005
OS | 4015 | 4015 | Y | Office | 056 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 15 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | Sf | 50 | - | - | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S013
OS | 4006 | 4006 | Y | Office | 057 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 2 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4002 | 4002 | Y | Office | 058 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4C01 |  | Y | Hallway | 059 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 49 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | 19 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S005
OS | 3002 | 3002 | Y | Office | 060 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material wa svisually similar to S003
[6 empty] | Mechanical | N/F
[6 empty] | Other | Fume Hood | Transite | P | A | N | Sf | 50 | - | - | VS013 | Transite | 20 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S013
OS | 3004 | 3004 | Y | Office | 061 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 7 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3008 | 3008 | Y | Office | 062 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material wa svisually similar to S003
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3009 | 3009 | Y | Office | 063 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS017 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S017
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3011 | 3011 | Y | Office | 064 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 3 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material was visually similar to S003.
OS | 3016 | 3016 | Y | Office | 065 | Floor | Tile | Vinyl tile | Y | A | N | Sf | 400 | - | - | S023 | 9' x 9' Beige with thick brown streaks | 6 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S024 was collected but not confirmed ACM. S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
OS | 3017 | 3017 | Y | Office | 066 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as the material was new.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
OS | 3000 | 3000 | Y | Office | 067 | Floor | Tile | Vinyl tile | P | A | N | Sf | 600 | - | - | VS023 | 9' x 9' Beige with thick brown streaks | 6 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S023
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
OS | 3001, 3001A | 3001 | Y | Office | 068 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3005 | 3005 | Y | Office | 069 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3010 | 3010 | Y | Office | 070 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3015 | 3015 | Y | Office | 071 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3C01 |  | Y | Hallway | 072 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 30 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2006 | 2006 | Y | Office | 073 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 5 | 1 | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2007 | 2007 | Y | Office | 074 | Floor | Tile | Vinyl tile | Y | A | N | SF | 30 | - | - | S025 | 12' x 12' Brown with thick dark brown streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 5 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
OS | 2000, 2000A | 2000 | Y | Office | 075 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 5 | 1 | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2001 | 2001 | Y | Office | 076 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 25 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2003 | 2003 | Y | Office | 077 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 16 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2C03 |  | Y | Hallway | 078 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 7 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2C02 |  | Y | Hallway | 079 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 11 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2C01 |  | Y | Hallway | 080 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 100 | - | - | VS020 | DWJC | 3 | - | - | - | - | - |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 2002 | 2002 | Y | Furnace Room | 081 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 100 | - | - | VS020 | DWJC | 3 | - | - | - | - | - |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Textile cloth | Y | A | N | LF | 5 | - | - | S027 | Textile cloth on ductwork | 50 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | Structure | Spray Fireproofing | Y | D | Y | Sf | 2 | - | 3 | S026 | Spray Fireproofing | 0 | 0 | 0 | 60 | 0 | 0
OS | 1000 | 1000 | Y | Office | 082 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 27 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1001, 1002 | 1001, 1002 | Y | Office | 083 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 27 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1012 | 1012 | Y | Cold Room | 084 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1011 | 1011 | Y | Cold Room | 085 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1009 | 1009 | Y | Office | 086 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1008 | 1008 | Y | Office | 087 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1007 | 1007 | Y | Mechanical Room | 088 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 1 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1006 | 1006 | Y | Electrical Room | 089 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1S01 |  | Y | Stairwrll | 090 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 4 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
AX | 1002 | 1002 | Y | Office | 091 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Tank | Insulation | P | A | Y | SF | 50 | - | - | VS007 | Tank Insulation | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S007
[6 empty] | Other | N/F
OS | 4001, 4001B, 4001A | 4001 | Y | Office | 046 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 13 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4011A | 4001 | Y | Office | 046 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 13 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4005, 4005A | 4005 | Y | Office | 048 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 4 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4017, 4017A | 4017 | Y | Office | 048 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 4 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4016, 4016A, 4016B | 4016 | Y | Office |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 5 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4SO1, 4S02, 3S01, 3S02 |  | Y | Stairwells |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4008, 4008A, 4008B | 4008 | Y | Office | 050 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 9 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4012, 4012A | 4012 | Y | Office | 053 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 2 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4014, 4014A, 4014B | 4014 | Y | lab/offices |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 10 | - | - | VS004 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S004
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1E01, 2E01, 3E01, 4E01 3E02 |  | Y | ELEVATOR | 058 | Floor |  | Steel | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall |  | Steel | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 4004 | 4004 | Y | Custodial Room |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 7 | - | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material wa svisually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3008, 3008A, 3008B | 3008 | Y | Office | 062 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material wa svisually similar to S003
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3012, 3012A, 3012B | 3012 | Y | Office |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material wa svisually similar to S003
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3014, 3014A | 3014 | Y | Office |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | NS | [6 empty] | VS003 | Parging Cement | [7 empty] | NS as the material wa svisually similar to S003
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3016, 3016A | 3016 | Y | Office | 065 | Floor | Tile | Vinyl tile | Y | A | N | Sf | 400 | - | - | VS023 | 9' x 9' Beige with thick brown streaks | 6 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as material is similar to S023
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS020 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S024 was collected but not confirmed ACM. S020 was confirmed ACM therefore all DWJC in the site building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3018 | 3018 | Y | Office | 066 | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
OS | 2006, 2006A | 2006 | Y | Office | 073 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 5 | 1 | - | VS005 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S005
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1010 | 1010 | Y | Cold Room |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1005 | 1005 | Y | Cold Room |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 1013 | 1013 | Y | Mechanical Room |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3003 | 3003 | Y | custodial room |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3007, 3007A, 3007B | 3007 | Y | lab |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | straight/fittings | Fiberglass | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
OS | 3013 | 3013 | Y | lab |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as wood is not suspect ACM
[6 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | straight/fittings | Fiberglass | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F