## Sheet1
Building | Room # | Room # (numeric) | Room Accessed (Y/N) | Location Description | PLEL Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[12 empty] | Unit of Measure | Condition
[13 empty] | Good | Fair | Poor
QC | 2001 | 2001 | Y | Office | 001 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 150 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S001 | 2' x 4' pinhole fleck
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S002 | 2' x 4' small fissure and hole
[6 empty] | Ceiling | Fixed | Stucco | Y | A | Y | SF | 149 | - | 1 | S003 | Stucco | 4 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2002 | 2002 | Y | Office | 002 | Floor | Vinyl Tile | Tile | N | [6 empty] | S004 | 12' x 12' White with small black streaks | [6 empty] | PLEL | No mastic analyzed.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 150 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2002A | 2002 | Y | Office | 003 | Floor | Vinyl Tile | Tile | NS | [6 empty] | VS004 | 12' x 12' White with small black streaks | [6 empty] | PLEL | NS as the material was visually similar to S004.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 150 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2003 | 2003 | Y | Office | 004 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 265 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2C01 |  | Y | Hallway | 005 | Floor |  | Terazzo | NS | [14 empty] | PLEL | NS as terazzo is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 1220 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | Sf | 1220 | - | - | VS003 | Stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1S01 - 4S01 |  | Y | Stairwell | 006 | Floor | Vinyl Tile | Tile | Y | A | N | Sf | 330 | - | - | S009 | 9' x 9' Brown with small black streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Vinyl Tile | Tile Mastic | N | [6 empty] | S009 | 9' x 9' Brown with small black streaks
[6 empty] | Wall | Fixed | Plaster | N | [6 empty] | S006 | Plaster | [7 empty] | single layer plaster
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 260 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Fixed | Stucco | Y | A | Y | SF | 330 | - | - | S007 | Stucco | 4 | 0 | 0 | 0 | 0 | 0
Piping
Mechanical
[6 empty] | Other | Light Fixture | Heat Shield | Y | D | N | EA | 4 | - | 1 | S008 | Incandescent heat shield | 70 | 0 | 0 | 0 | 0 | 0
QC | 2005 | 2005 | Y | Washroom | 007 | Floor | Sheet Flooring | VSF | N | [6 empty] | S010 | Beige | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S010 | Beige
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2006 | 2006 | Y | Washroom | 008 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS010 | Beige | [6 empty] | PLEL | NS as the material was visually similar to S010
[6 empty] | Floor | Sheet Flooring | VSF Mastic | NS | [6 empty] | VS010 | Beige | [7 empty] | NS as the material was visually similar to S010
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2011 | 2011 | Y | Office | 009 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Fixed | Stucco | P | A | Y | SF | 2600 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Wall | Fixed | Plaster | N | [6 empty] | S011 | Plaster | [7 empty] | NS as the material was visually similar to S011
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 2280 | 20 | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f | [17 empty] | No access above ceiling.
QC | 2008 | 2008 | Y | Office | 010 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 240 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 240 | 20 | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2007 | 2007 | Y | Office | 011 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 240 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 240 | 20 | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2010 | 2010 | Y | Office | 012 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 240 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 240 | 20 | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2009 | 2009 | Y | Office | 013 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 240 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 240 | 20 | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2019 | 2019 | Y | Office | 014 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2015 | 2015 | Y | Storage Room | 015 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2018 | 2018 | Y | Office | 016 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2014 | 2014 | Y | Office | 017 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | Y | A | N | SF | 200 | - | - | S012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2014A | 2014 | Y | Office | 018 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2C02 |  | Y | Hallway | 019 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 2E01 |  | Y | Elevator | 020 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[6 empty] | Ceiling |  | Plastic | NS | [15 empty] | NS as plastic is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2S02 |  | Y | Stairwell | 021 | Floor | Vinyl Tile | Tile | P | A | N | SF | - | 90 | - | VS009 | 9' x 9' Brown with small black streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[6 empty] | Floor | Vinyl Tile | Tile Mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with small black streaks | [7 empty] | NS as the material was visually similar to S009
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Fixed | Stucco | P | A | N | SF | 250 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2013 | 2013 | Y | Office | 022 | Floor | Vinyl Tile | Tile | P | A | N | SF | - | 90 | - | VS009 | 9' x 9' Brown with small black streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[6 empty] | Floor | Vinyl Tile | Tile Mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with small black streaks | [7 empty] | NS as the material was visually similar to S009
[6 empty] | Floor | Vinyl Tile | Tile | Y | A | N | SF | 870 | - | - | S013 | 12' x 12' Brown with thick grey and white streaks | 4 | 0 | 0 | 0 | 0 | 0
[6 empty] | Floor | Vinyl Tile | Tile Mastic | Y | D | N | SF | 870 | - | - | S013 | 12' x 12' Brown with thick grey and white streaks | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Floor | Vinyl Tile | Tile | N | [6 empty] | S014 | 12' x 12' White with red streaks
[6 empty] | Floor | Vinyl Tile | Tile Mastic | N | [6 empty] | S014 | 12' x 12' White with red streaks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 930 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 2012 | 2012 | Y | Office | 023 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 200 | - | - | S015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Straight Run | Insulation | N | [6 empty] | S016 | Straight Pipe Insulation - tan layer
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | Y | D | Y | EA |  |  | 1 | S017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0
QC | 1018 | 1018 | Y | Janitor's Closet | 024 | Floor | Vinyl Tile | Tile | Y | A | N | SF | 25 | - | - | S018 | 9' x 9' Black | 4 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Vinyl Tile | Tile Mastic | Y | A | N | Sf | 25 | - | - | S018 | 9' x 9' Black | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 50 | - | - | S019 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | Straight Run | Insulation | N | [6 empty] | S016 | Straight Pipe Insulation - black layer
[6 empty] | Mechanical | Light Fixture | Heat Shield | P | D | N | EA | - | - | 1 | VS008 | Incandescent heat shield | 70 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S008
[6 empty] | Other | Elbows/Fittings | Parging Cement | Y | D | Y | EA |  |  | 1 | S017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0
QC | 1018A | 1018 | Y | Office | 025 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 1019 | 1019 | Y | Office | 026 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S020 | 2' x 2' pinhole fleck
[6 empty] | Piping | Straight Run | Insulation | NS | [6 empty] | VS016 | Straight Pipe Insulation | [7 empty] | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | - | 6 | 2 | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S017
QC | 1020 | 1020 | Y | Office | 027 | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1000 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 1000 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 1004A | 1004 | Y | Office | 028 | Floor | Vinyl Tile | Tile | N | [6 empty] | S021 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL
[6 empty] | Floor | Vinyl Tile | Tile Mastic | N | [6 empty] | S021 | 12' x 12' White with abundant grey flecks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1000 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 1000 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1004 | 1004 | Y | Office | 029 | Floor | Vinyl Tile | Tile | P | A | N | SF | 815 | - | - | VS018 | 9' x 9' Black | 4 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S018
[6 empty] | Floor | Vinyl Tile | Tile Mastic | P | A | N | Sf | 815 | - | - | VS018 | 9' x 9' Black | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S018
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S001
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | Limited access above the ceiling
QC | 1005 | 1005 | Y | Office | 030 | Floor | Vinyl Tile | Tile | P | A | N | SF | 815 | - | - | VS018 | 9' x 9' Black | 4 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S018
[6 empty] | Floor | Vinyl Tile | Tile Mastic | P | A | N | Sf | 815 | - | - | VS018 | 9' x 9' Black | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S018
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 900 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S001
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | Limited access above the ceiling
QC | 1C01 |  | Y | Hallway | 031 | Floor | Vinyl Tile | Tile | P | A | N | SF | 800 | - | - | VS009 | 9' x 9' Brown with black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[6 empty] | Floor | Vinyl Tile | Tile Mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with black streak | [7 empty] | NS as the material was visually similar to S009
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 800 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1021 | 1021 | Y | Office | 032 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Wood | NS | [15 empty] | NS as wood is not suspect ACM.
[6 empty] | Piping | Straight Run | Insulation | NS | [6 empty] | VS016 | Straight Pipe Insulation | [7 empty] | NS as the material was visually similar to S016.
[6 empty] | Mechanical | Light Fixture | Heat Shield | P | D | N | EA | 2 | - | 1 | VS008 | Incandescent heat shield | 70 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S008
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | - | 6 | 2 | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S017
QC | 1021A | 1021 | Y | Office | 033 | Floor |  | Cement Board | Y | A | N | SF | - | - | 12 | S023 | Cement Board | 15 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling |  | Plaster | N | [6 empty] | S022 | Plaster | [7 empty] | both layers none detected
[6 empty] | Piping | Straight Run | Insulation | NS | [6 empty] | VS016 | Straight Pipe Insulation | [7 empty] | NS as the material was visually similar to S016.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA | - | 6 | 2 | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S017
QC | 1003 | 1003 | Y | Office | 034 | Floor |  | Wood | NS | [14 empty] | PLEL | NS as wood is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 400 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually the same as S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1S01 |  | Y | Stairwell | 035 | Floor | Vinyl Tile | Tile | P | A | N | SF | 100 | - | - | VS009 | 9' x 9' Brown with black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[6 empty] | Floor | Vinyl Tile | Tile Mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with black streak | [7 empty] | NS as the material was visually similar to S009
[6 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 100 | - | - | S024 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 100 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1006 | 1006 | Y | Office | 036 | Floor | Vinyl Tile | Tile | P | A | N | SF | 100 | - | - | VS009 | 9' x 9' Brown with black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[6 empty] | Floor | Vinyl Tile | Tile Mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with black streak | [7 empty] | NS as the material was visually similar to S009
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS024 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall |  | Plaster | N | [6 empty] | S025 | Plaster | [7 empty] | both layers none detected
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 100 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1007 | 1007 | Y | Office | 037 | Floor | Vinyl Tile | Tile | Y | A | N | SF | 330 | - | - | S026 | 9' x 9' Brown with thick grey and white streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Vinyl Tile | Tile Mastic | Y | D | N | SF | 330 | - | - | S026 | 9' x 9' Brown with thick grey and white streaks | 5 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 330 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 1000 | 1000 | Y | Office | 038 | Floor | Sheet Flooring | VSF | NS | [14 empty] | PLEL | NS as the material is new.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 450 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 4 | - | - | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S017
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 1009 | 1009 | Y | Office | 039 | Floor | Vinyl Tile | Tile | P | A | N | SF | 100 | - | - | VS009 | 9' x 9' Brown with black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[6 empty] | Floor | Vinyl Tile | Tile Mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with black streak | [7 empty] | NS as the material was visually similar to S009
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 100 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 100 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 4 | 0 | - | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S017
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1012 | 1012 | Y | Office | 040 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 1014 | 1014 | Y | Office | 041 | Floor | Vinyl Tile | Tile | N | [6 empty] | S027 | 12' x 12' Blue with abundant white flecks | [6 empty] | PLEL
[6 empty] | Floor | Vinyl Tile | Tile Mastic | Y | D | N | Sf | 450 | - | - | S027 | 12' x 12' Blue with abundant white flecks | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 450 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 1 | - | - | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S017
[6 empty] | Mechanical | N/F
[6 empty] | Other | Structure | Tar Mastic | Y | D | N | SF | 450 | - | - | S028 | Tar on foam insulation | 10 | 0 | 0 | 0 | 0 | 0 |  | tar on foam insulation
QC | 1015 | 1015 | Y | Office | 042 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 1C02 |  | Y | Hallway | 042 | Floor | Vinyl Tile | Tile | NS | [6 empty] | VS021 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S021
[6 empty] | Floor | Vinyl Tile | Tile Mastic | NS | [6 empty] | VS021 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S021
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 600 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 600 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4C01, 4C02, 4C03 |  | Y | Hallway | 043 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1600 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S001
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Structure | Cement | Y | D | N | SF | - | 3 | - | S029 | Cement | 5 | 0 | 0 | 0 | 0 | 0 |  | above ceiling
QC | 3C01 |  | Y | Hallway | 044 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 1700 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 1 | 0 | 0 | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S017
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Insulation | NS | [6 empty] | VS016 | Straight Pipe Insulation | [7 empty] | NS as the material was visually similar to S016.
QC | 3005 | 3005 | Y | Office | 045 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 600 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3005, 3005A | 3005 | Y | Office | 046 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 520 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S030 was collected but not confirmed ACM. S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Wall |  | Plaster | N | [6 empty] | S031 | Plaster | [7 empty] | both layers none detected
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3007 | 3007 | Y | Office | 047 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3010 | 3010 | Y | Office | 048 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3014 | 3014 | Y | Office | 049 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3015 | 3015 | Y | Office | 050 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3016A | 3016 | Y | Office | 051 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 150 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3016 | 3016 | Y | Office | 052 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 150 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3016B | 3016 | Y | Office | 053 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as the material was new.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 70 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 70 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 3019 | 3019 | Y | Office | 054 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 40 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Wall |  | Plaster | N | [6 empty] | S032 | Plaster | [7 empty] | both layers none detected
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3020 | 3020 | Y | Office | 055 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 40 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3021 | 3021 | Y | Office | 056 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3022 | 3022 | Y | Office | 057 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3000 | 3000 | Y | Office | 058 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3000A | 3000 | Y | Office | 059 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3000B | 3000 | Y | Office | 060 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [15 empty] | NS as the material was new.
[6 empty] | Ceiling | Fixed | Stucco | P | D | Y | SF | 329 | - | 1 | VS003 | Stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually simlar to S003
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3000C | 3000 | Y | Office | 061 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' small fissure and pinhole | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3000D | 3000 | Y | Office | 062 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' small fissure and pinhole | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3001 | 3001 | Y | Office | 063 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' small fissure and pinhole | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3002 | 3002 | Y | Office | 064 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' small fissure and pinhole | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3002A | 3002 | Y | Office | 065 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' small fissure and pinhole | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3003 | 3003 | Y | Office | 066 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | Y | A | N | Sf | 225 | - | - | S033 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' small fissure and pinhole | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3004 | 3004 | Y | Office | 067 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 60 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3008 | 3008 | Y | Office | 068 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 60 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3009 | 3009 | Y | Office | 069 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S001
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 3011 | 3011 | Y | Office | 070 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 50 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | Sf | 50 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 3012 | 3012 | Y | Office | 071 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S001
[6 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 15 | - | - | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S017
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 4001A | 4001 | Y | Office | 072 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Above ceiling | Stucco | Y | D | Y | SF | 400 | - | - | S035 | Stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | above ceiling tiles
QC |  |  | y | Office | 073 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 4001 | 4001 | Y | Office | 074 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | Above ceiling | Stucco | P | D | Y | SF | 400 | - | - | VS035 | Stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S035
QC | 4000 | 4000 | Y | Office | 075 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 400 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually similar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 4028 | 4028 | Y | Office | 076 | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[6 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 720 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS001 | 2' x 4' pinhole fleck | [7 empty] | NS as the material was visually similar to S001
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 4024 | 4024 | Y | Office | 077 | Floor | Sheet Flooring | VSF | N | [6 empty] | S036 | White with blue specks | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S036 | White with blue specks
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4016 | 4016 | Y | Office | 078 | Floor | Sheet Flooring | VSF | N | [6 empty] | S037 | Brown stone pattern | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S037 | Brown stone pattern
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4012 | 4012 | Y | Office | 079 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Drywall | DWJC | Y | A | N | SF | 250 | - | - | S038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | used to level plaster above ceiling
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4020 | 4020 | Y | Office | 080 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 4010 | 4010 | Y | Office | 081 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 4009 | 4009 | Y | Office | 082 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 4003 | 4003 | Y | Office | 083 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS020 | 2' x 2' pinhole fleck | [7 empty] | NS as the material was visually simlar to S020
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
QC | 1003A | 1003 | Y | Office | 002 |  | Floor |  | WOOD | N | [14 empty] | PLEL | Ns as material is non suspect ACM
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 305 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[7 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 150 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 1S01, 2S01, 3S01, 4S01 |  | Y | Stairwell | 006 |  | Floor | Tile | Vinyl tile | Y | A | N | Sf | 330 | - | - | S009 | 9' x 9' Brown with small black streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL
[7 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S009 | 9' x 9' Brown with small black streaks
[7 empty] | Wall | Fixed | Plaster | N | [6 empty] | S006 | Plaster
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 260 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[7 empty] | Ceiling | Fixed | Stucco | Y | A | Y | SF | 330 | - | - | S007 | Stucco | 4 | 0 | 0 | 0 | 0 | 0
[7 empty] | Piping | NF
[7 empty] | Mechanical | NF
[7 empty] | Other | Light Fixture | Heat Shield | Y | D | N | EA | 4 | - | 1 | S008 | Incandescent heat shield | 70 | 0 | 0 | 0 | 0 | 0
QC | 3018 | 3018 | Y | CLOSET |  |  | Floor | Sheet Flooring | VSF | N | [6 empty] | S040 | Light grey with grey streaks - tile only | [6 empty] | PLEL
[7 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 120 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM all DWJC should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [5 empty] | - | VS02 | 2' x 4' small fissure and hole
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1010 | 1010 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 240 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[7 empty] | Structure |  | not insulated
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 1E01, 2E01, 3E01, 4E01 |  | Y | Elevator | 020 |  | Floor |  | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[7 empty] | Wall |  | Steel | NS | [15 empty] | NS as steel is not suspect ACM.
[7 empty] | Ceiling |  | Plastic | NS | [15 empty] | NS as plastic is not suspect ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 1S01, 2S02, 3S03, 4S04 |  | Y | Stairwell | 021 |  | Floor | Tile | Vinyl tile | P | A | N | SF | - | 90 | - | VS009 | 9' x 9' Brown with small black streaks | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[7 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with small black streaks | [7 empty] | NS as the material was visually similar to S009
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[7 empty] | Ceiling | Fixed | Stucco | P | A | N | SF | 250 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 2012 | 2012 | Y | CLOSET | 023 |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 200 | - | - | S015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[7 empty] | Piping | Straight Run | Insulation | N | [6 empty] | VS016 | Straight Pipe Insulation
[7 empty] | Mechanical | N/F
[7 empty] | Other | Elbows/Fittings | Parging Cement | Y | D | Y | EA |  |  | 1 | S017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0
QC | 1014a | 1014 | Y | Mechanical |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS015 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[7 empty] | Piping | Straight Run | Insulation | NS | [6 empty] | VS016 | Straight Pipe Insulation
[7 empty] | Mechanical | N/F
QC | 1018 1018A | 1018 | Y | Janitor's Closet | 024 |  | Floor | Tile | Vinyl tile | Y | A | N | SF | 25 | - | - | S018 | 9' x 9' Black | 4 | 0 | 0 | 0 | 0 | 0 | PLEL
[7 empty] | Floor | Tile | Tile mastic | Y | A | N | Sf | 25 | - | - | S018 | 9' x 9' Black | 3 | 0 | 0 | 0 | 0 | 0
[7 empty] | Wall | Drywall | DWJC | Y | A | N | SF | 50 | - | - | S019 | DWJC | 3 | 0 | 0 | 0 | 0 | 0
[7 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[7 empty] | Piping | Straight Run | Insulation | N | [6 empty] | S016 | Straight Pipe Insulation | [7 empty] | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Mechanical | Light Fixture | Heat Shield | P | D | N | EA | - | - | 1 | VS008 | Incandescent heat shield | 70 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S008
[7 empty] | Other | Elbows/Fittings | Parging Cement | P | D | Y | EA |  |  | 1 | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0
QC | 1018B | 1018 | Y | Storage Room | 025 |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[7 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[7 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 1011 | 1011 | Y | Mech Room |  |  | Floor/Wall Ceiling | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[7 empty] | Pipe | Straight | Fiberglass | NS | [15 empty] | Ns as material is non suspect ACM
[7 empty] | Mechanical | Tank 1 | Parging Cement | P | D | Y | SF | 120 |  |  | VS017 | Parging Cement | 30 | [6 empty] | Confirmed ACM
[7 empty] | Mechanical | Tank 2 | Parging Cement | P | D | Y | SF | 120 |  |  | VS017 | Parging Cement | 30 | [6 empty] | Confirmed ACM
[7 empty] | Mechanical | Tank 3 | Parging Cement | P | D | Y | SF | 100 |  |  | VS017 | Parging Cement | 30 | [6 empty] | Confirmed ACM
[7 empty] | Piping | Elbows/Fittings | Parging Cement | P | D | Y | EA | 14 |  |  | VS017 | Parging Cement | 30 | 0 | 0 | 0 | 0 | 0
QC | 1020A,1020B | 1020 | Y | MECHANICAL |  |  | Floor | Concrete | Concrete | [15 empty] | PLEL | Ns as material is non suspect ACM
[7 empty] | Wall | Concrete | Concrete | [16 empty] | Ns as material is non suspect ACM
[7 empty] | Ceiling | Concrete | Concrete | [16 empty] | Ns as material is non suspect ACM
[7 empty] | Piping | N/F
[7 empty] | Mechanical | Ducts | Fiberglass | NS
[7 empty] | Other | N/F
QC | 2012A | 2012 | Y | MECHANICAL |  |  | Floor | Concrete | Concrete | [15 empty] | PLEL | Ns as material is non suspect ACM
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[7 empty] | Ceiling | Concrete | Concrete | [16 empty] | Ns as material is non suspect ACM
[7 empty] | Piping | N/F
[7 empty] | Mechanical | Ducts | Fiberglass | NS
[7 empty] | Other | N/F
QC | 2012A | 2012 | Y | MECHANICAL |  |  | Floor | tile | Vinyl tile | NS | [6 empty] | VS039 | 12' x 12' GREY W/ GREY FLECK | [6 empty] | PLEL | NS AS MATERIAL IS SIMILAR TO S039
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 150 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[7 empty] | Ceiling | Concrete | Concrete | [16 empty] | Ns as material is non suspect ACM
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 1S03, 1S02 |  | Y | Stairwell | 035 |  | Floor | Tile | Vinyl tile | P | A | N | SF | 100 | - | - | VS009 | 9' x 9' Brown with black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S009
[7 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS009 | 9' x 9' Brown with black streak | [7 empty] | NS as the material was visually similar to S009
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 350 | - | - | VS024 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 100 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1008 | 1008 | Y | Office |  |  | Floor | Tile | Vinyl tile | P | A | N | SF | 241 | - | - | VS013 | 12' x 12' Brown with thick grey and white streaks | 4 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S013
[7 empty] | Floor | Tile | Tile mastic | P | D | N | SF | 241 | - | - | VS013 | 12' x 12' Brown with thick grey and white streaks | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 560 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 1008 | 1008 | Y | W'RM |  |  | Floor | Tile | Vinyl tile | P | A | N | SF | 27 | - | - | VS013 | 12' x 12' Brown with thick grey and white streaks | 4 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S013
[7 empty] | Floor | Tile | Tile mastic | P | D | N | SF | 27 | - | - | VS013 | 12' x 12' Brown with thick grey and white streaks | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S013
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 27 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 3013 | 3013 | Y | ELECT |  |  | Floor | tile | Vinyl tile | N | [6 empty] | S039 | 12' x 12' GREY W/ GREY FLECK | [6 empty] | PLEL
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 145 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC should be presumed ACM.
[7 empty] | Ceiling | Concrete | Concrete | NS | [15 empty] | Ns as material is non suspect ACM
[7 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | Ns as material is non suspect ACM
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
GC | 2017 | 2017 | Y | OFFICE |  |  | Floor | Carpet | Carpet | NS | [15 empty] | Non Suspect ACM
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 50 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 27 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 1C02 |  | Y | Hallway | 042 |  | Floor | Tile | Vinyl tile | NS | [6 empty] | VS021 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S021
[7 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS021 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S021
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 800 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Fixed | Stucco | P | A | Y | SF | 600 | - | - | VS003 | stucco | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 1014B |  | Y | office |  |  | Floor | Tile | Vinyl tile | NS | [6 empty] | VS021 | 12' x 12' White with abundant grey flecks | [6 empty] | PLEL | NS as the material was visually similar to S021
[7 empty] | Floor | Tile | Tile mastic | NS | [6 empty] | VS021 | 12' x 12' White with abundant grey flecks | [7 empty] | NS as the material was visually similar to S021
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 151 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2X4 small fissure | [7 empty] | NS as the material was visually similar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 3006 | 3006 | Y | Office | 045 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | Sf | 600 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [7 empty] | new material | [7 empty] | NS as the material was new.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 3004, 3004A | 3004 | Y | Office | 067 |  | Floor | Sheet Flooring | Rubber | NS | [14 empty] | PLEL | NS as rubber is not suspect Acm.
[7 empty] | Wall | Drywall | DWJC | P | A | n | Sf | 60 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually similar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 4016 | 4016 | Y | Office | 078 |  | Floor | Sheet Flooring | Vinyl | N | [6 empty] | S037 | Brown stone pattern | [6 empty] | PLEL
[7 empty] | Floor | Sheet Flooring | Vinyl Mastic | N | [6 empty] | S037 | Brown stone pattern
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 500 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 200 | - | - | VS012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4012 | 4012 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | Y | A | N | SF | 250 | - | - | S038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4013 | 4013 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4015 | 4015 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4017 | 4017 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4018 | 4018 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4019 | 4019 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
DQ | 4021 | 4021 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4023 | 4023 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4024 | 4034 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4025 | 4025 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4026 | 4026 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4027 | 4027 | Y | Office | 079 |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 550 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Drywall | DWJC | P | A | N | SF | 250 | - | - | VS038 | DWJC | 4 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F | [17 empty] | No access above ceiling.
QC | 4008 | 4008 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 4007 | 4007 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 4006 | 4006 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 4005 | 4005 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 4004 | 4004 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F
QC | 4011, 4011a | 4011 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Floor | Tile | Vinyl tile | N | [6 empty] | S041 | 12X12 BLUE GREY TILES
[7 empty] | Floor | Tile | Tile mastic | N | [6 empty] | S041 | 12X12 BLUE GREY TILES
QC | 4014 | 4014 | Y | Office |  |  | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[7 empty] | Wall | Drywall | DWJC | P | A | N | SF | 300 | - | - | SV012 | DWJC | 3 | 0 | 0 | 0 | 0 | 0 |  | S012 was confirmed ACM therefore all DWJC in the building should be presumed ACM.
[7 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 4' small fissure and hole | [7 empty] | NS as the material was visually simlar to S002
[7 empty] | Piping | N/F
[7 empty] | Mechanical | N/F
[7 empty] | Other | N/F