## Sheet1
Building | Room # | Room # (numeric) | Room Access (Y/N) | Location Description | PLEL Location # | System | Component | Material | ACM (Y/N/P/NS) | Access (A/B/C/D) | Friable (Y/N) | ACM Quantity/Condition |  |  |  | Sample # | Sample Description | % Chrysotile | % Crocidolite | % Tremolite | % Amosite | % Anthophylite | % Actinolite | Surveyor | Comments
[12 empty] | Unit of Measure | Condition
[13 empty] | Good | Fair | Poor
J | 2000 B | 2000 | Y | Conference Room | 001 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as DWJC on the ceiling was sampled.
[6 empty] | Ceiling | Drywall | DWJC | N | [6 empty] | S001 | DWJC
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | N | [6 empty] | S002 | 2' x 2' pinhole fissure
[6 empty] | Piping | Elbows/Fittings | Parging cement | Y | D | Y | EA | - | 2 | - | S003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
J | 2000 | 2000 | Y | Main Office | 002 | Floor | Tile | Tile Mastic | Y | D | N | SF | 400 | - | - | S004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Vinyl Tile | N | [6 empty] | S004 | 12' x 12' White with abundant brown flecks
[6 empty] | Wall | Drywall | DWJC | NS
[6 empty] | Wall |  | Plaster | P | A | N | SF | 400 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | - | 1 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | N | [6 empty] | S005 | Tar mastic
[6 empty] | Piping | Straight Run | Tar paper | N | [6 empty] | S006 | Tar paper
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
J | 2000 C, 2000 D | 2000 | Y | Photocopy/Storage Room | 003 | Floor | Tile | Vinyl Tile | N | [6 empty] | S008 | 12' x 12' Grey with abundant grey and white flecks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile Mastic | N | [6 empty] | S008 | Grey with abundant grey and white flecks
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS
[6 empty] | Wall |  | Plaster | P | A | N | SF |  |  |  | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Drywall | DWJC | NS
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 2000 A | 2000 | Y | Office | 004 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | Ea | - | 1 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | Behind heaters | Transite | Y | D | N | SF | 11 | - | <1 | S009 | Transite behind heaters | 15 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
J | 2019 | 2019 | Y | Office | 005 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as DWJC was sampled in a representative # of locations.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S007.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2018 | 2018 | Y | Office | 006 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as DWJC was sampled in a representative # of locations.
[6 empty] | Wall |  | Plaster | Y | A | N | SF | 280 | - | - | S010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | base layer (#1) was ACM
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | 2 | - | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2002 | 2002 | Y | Office | 007 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
Wall
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002/
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | - | 1 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2003 | 2003 | Y | Office | 008 | Floor | Tile | Tile Mastic | P | D | N | SF | 180 | - | - | VS004 | Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl Tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 180 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S007.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | - | 1 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2004 | 2004 | Y | Office | 009 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Wall | Plaster | Plaster | P | A | N | SF | 112 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S007; The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | Ea | - | 1 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2017 | 2017 | Y | Office | 010 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S011 | DWJC
[6 empty] | Wall |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2016 | 2016 | Y | Office | 011 | Floor | Tile | Tile Mastic | P | D | N | SF | 140 | - | - | VS004 | Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl Tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Wall |  | pLaster | P | A | N | SF | 140 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Straight Run | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2014 | 2014 | Y | Meeting Room | 012 | Floor | Tile | Vinyl Tile | N | [6 empty] | S012 | 12' x 12' Light grey with black streaks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile Mastic | N | [6 empty] | S012 | 12' x 12' Light grey with black streaks
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 240 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2C01 |  | Y | Hallway | 013 | Floor | Sheet Flooring | VSF Mastic | Y | D | N | SF | 250 | - | - | S013 | Mastic - grey with grey and white flecks | 4 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Sheet Flooring | VSF | N | [6 empty] | S013 | Light grey with grey and white flecks
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | Ductwork | Fiberglass | NS | [15 empty] | NS as fiberglass is not suspect ACM.
[6 empty] | Other | N/F
J | 2C02 |  | Y | Hallway | 014 | Floor | Sheet Flooring | VSF Mastic | P | D | N | SF | 500 | - | - | VS013 | Mastic - grey with grey and white flecks | 4 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S013.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS013 | Light grey with grey and white flecks | [7 empty] | NS as the material was visually similar to S013.
Wall
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | 30 | - | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | NS | [6 empty] | VS005 | Tar mastic | [7 empty] | NS as the material was visually similar to S005.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2C03 |  | Y | Hallway | 015 | Floor | Sheet Flooring | VSF Mastic | P | D | N | SF | 240 | - | - | VS013 | Mastic -light grey with grey and white flecks | 4 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S013.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS013 | Light grey with grey and white flecks | [7 empty] | NS as the material was visually similar to S013.
Wall
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | NS | [6 empty] | VS005 | Tar mastic | [7 empty] | NS as the materialw as visually similar to S005.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
J | 2005 | 2005 | Y | Office | 016 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | Ea | - | 2 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | NS | [6 empty] | VS005 | Tar mastic | [7 empty] | NS as the material was visually similar to S005.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2006 | 2006 | Y | Women's Washroom | 017 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 219 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 219 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 2007 | 2007 | Y | Men's Washroom | 018 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 219 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 219 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 2008 | 2008 | Y | Classroom | 019 | Floor | Sheet Flooring | VSF | N | [6 empty] | S014 | Beige speckled pattern | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S014 | Beige speckled pattern
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S015 | DWJC
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2009 A, 2009 B | 2009 | Y | Office | 020 | Floor | Tile | Tile Mastic | P | D | N | SF | 340 | - | - | VS004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl Tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | - | 10 | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | A | Y | EA | - | 1 | 1 | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2010 | 2010 | Y | Women's Washroom | 021 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | A | Y | EA | - | 2 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2011 | 2011 | Y | Custodian's Closet | 022 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 30 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [15 empty] | ` |  | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 2012 | 2012 | Y | Men's Washroom | 023 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | A | Y | EA | - | 2 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2013 | 2013 | N | Viewing Room | 024 | Floor | [17 empty] | PLEL
Wall
Ceiling
Piping
Mechanical
[6 empty] | Other | [18 empty] | No access to this room.
J | 2C04 |  | Y | Hallway | 025 | Floor | Sheet Flooring | VSF | N | [6 empty] | S018 | Blue VSF | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S018 | Blue VSF
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S017 | DWJC
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | Elbows/Fittings | Tar mastic | NS | [6 empty] | VS005 | Tar mastic | [7 empty] | NS as the material was visually similar to S005.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2V02 |  | Y | Entrance | 026 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 60 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Transite | P | A | N | SF | 60 | - | - | VS009 | Transite | 15 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S009.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | Exterior doors | Caulking | Y | A | N | LF | 40 | - | - | S019 | Grey caulking | 3 | 0 | 0 | 0 | 0 | 0
J | 2025 | 2025 | Y | Church | 027 | Floor | Sheet Flooring | VSF Mastic | Y | D | N | SF | 2200 | - | - | S022 | Mastic - grey speckled VSf | 3 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Sheet Flooring | VSF | N | [6 empty] | S022 | Grey speckled VSF
[6 empty] | Wall |  | Plaster | P | A | N | SF | 60 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Panel | Wood | NS | [15 empty] | NS as wood fibre is not suspect ACM>
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2024 | 2024 | Y | Sacristy | 028 | Floor | Tile | Vinyl Tile | Y | A | N | SF | 120 | - | - | S023 | 9' x 9' Brown with thick black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Tile Mastic | Y | D | N | SF | 120 | - | - | S023 | 9' x 9' Mastic | 3 | 0 | 0 | 0 | 0 | 0
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 120 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 2V03 |  | Y | Entrance | 029 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Brick | NS | [15 empty] | NS as brick is not suspect ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 40 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2V01 |  | Y | Entrance | 030 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 75 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material is visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2S01 |  | Y | Stairwell | 031 | Floor | Tile | Tile Mastic | P | D | N | SF | 20 | - | - | VS004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl Tile | NS | [6 empty] | VS012 | 12' x 12' Light grey with black streaks | [7 empty] | NS as the material was visually similar to S012.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2S02 |  | Y | Stairwell | 031 | Floor | Tile | Tile Mastic | P | D | N | SF | 125 | 0 | 0 | VS004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl Tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl Tile | Y | A | N | SF | 210 | - | - | S024 | 9' x 9' Brown with brown streak | 5 | 0 | 0 | 0 | 0 | 0 |  | Insufficient mastic to analyze.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Parging cement | Y | D | Y | SF | 63 | - | - | S026 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | parging cement on ducts
[6 empty] | Other | N/F
J | 2S03 |  | Y | Stairwell | 032 | Floor | Tile | Vinyl Tile | P | A | N | SF | 4 | - | - | VS023 | 9' x 9' Brown with thick black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S023.
[6 empty] | Floor | Tile | Tile Mastic | P | D | N | SF | 4 | - | - | VS023 | Brown with thick black streak | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S023.
[6 empty] | Floor | Tile | Vinyl Tile | P | A | N | SF | 150 | - | - | VS024 | 9' x 9' Brown with brown streaks | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S024. Insufficient mastic to analyze.
[6 empty] | Floor | Tile | Vinyl Tile | N | [6 empty] | S027 | 12' x 12' Brown with abundant brown
[6 empty] | Floor | Tile | Tile Mastic | N | [6 empty] | S027 | Brown with abundant brown
[6 empty] | Wall |  | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
J | 1C01 |  | Y | Hallway | 033 | Floor |  | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | A | Y | EA | 30 | - | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 3C01, 3C02, 3C03 |  | Y | Hallway | 034 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS013 | Grey with light grey and white | [6 empty] | PLEL | NS as the material was visually the same as S013
[6 empty] | Floor | Sheet Flooring | VSF Mastic | P | D | N | SF | 800 | - | - | VS013 | Grey with light grey and white | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually the same as S013.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 800 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 3010 | 3010 | Y | Staff Break Room | 035 | Floor | Tile | Vinyl Tile | P | A | N | SF | 125 | - | - | VS024 | 9' x 9' Brown with thick black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually the same as S024. Insufficient mastic to analyze.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 125 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3012 | 3012 | Y | Society Room | 036 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 250 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3014 | 3014 | Y | Computer Lab. | 037 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3015 | 3015 | Y | Seminar Room | 038 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3018 | 3018 | Y | Office | 039 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3025 | 3025 | Y | Janitor's Closet | 040 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | pLASTER | P | A | N | SF | 40 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/f | [17 empty] | No access above ceiling.
J | 3003 | 3003 | Y | Office | 041 | Floor | Tile | Tile Mastic | P | D | N | SF | 250 | - | - | VS004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl Tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 250 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3007 | 3007 | Y | Female Washroom | 042 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 300 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S030 | DWJC
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 300 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3008 | 3008 | Y | Classroom | 043 | Floor | Tile | Vinyl Tile | P | A | N | SF | 250 | - | - | VS023 | 9' x 9' Brown with thick black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S023.
[6 empty] | Floor | Tile | Tile Mastic | P | D | N | SF | 250 | - | - | VS023 | Brown with thick black streak | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S023.
[6 empty] | Floor | Tile | Vinyl Tile | P | A | N | SF | 275 | - | - | VS024 | 9' x 9' Brown with brown streaks | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S024. Insufficient mastic to analyze.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Texture | Stucco | N | [6 empty] | S032 | Stucco
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 3016 | 3016 | Y | Office | 044 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | - | 4 | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the materialw as visually similar to S003.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | Structural steel | Cementious | Y | D | Y | SF | - | 150 | - | S033 | Cementious material | 5 | 0 | 0 | 0 | 0 | 0 |  | cementitious material on structural steel above ceiling
J | 3013 | 3013 | Y | Supply Room | 045 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S034 | DWJC
[6 empty] | Ceiling |  | Plaster | P | A | N | SF |  |  |  | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/f | [17 empty] | No access above ceiling.
J | 3019 | 3019 | Y | Office | 046 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3020 | 3020 | Y | Office | 047 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3021 | 3021 | Y | Office | 048 | Floor | Sheet Flooring | VSF | N | [6 empty] | S035 | Beige VSF | [6 empty] | PLEL
[6 empty] | Floor | Sheet Flooring | VSF Mastic | N | [6 empty] | S035 | Beige VSf
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 250 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3022 | 3022 | Y | Filing Room | 049 | Floor | Tile | Tile Mastic | Y | D | N | SF | 175 | - | - | S036 | 12' x 12' Mastic | 2 | 0 | 0 | 0 | 0 | 0 | plel
[6 empty] | Floor | Tile | Vinyl Tile | N | [6 empty] | S036 | 12' x 12' Beige with brown streak tile
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 175 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3023 | 3023 | Y | Office | 050 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 175 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3024 | 3024 | Y | Office | 051 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 200 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3000 | 3000 | Y | Office | 052 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 250 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3001 | 3001 | Y | Office | 053 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 250 | - | - | VS010 | Plaster | 250 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3002 | 3002 | Y | Office | 054 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 250 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 3009 | 3009 | Y | Lunchroom | 055 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | TExture | Stucco | NS | [6 empty] | VS032 | Stucco | [7 empty] | NS as the material was visually similar to S032.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4008 | 4008 | Y | Office | 056 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | N/F | [17 empty] | Limited access above the ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | Limited access above the ceiling.
[6 empty] | Other | Above ceiling tile | Stucco | Y | D | Y | SF | 125 | 1 | - | S037 | Stucco | 5 | 0 | 0 | 0 | 0 | 0
J | 4009 | 4009 | Y | Closet | 057 | Floor | Tile | Tile Mastic | Y | D | N | SF | 12 | - | - | S038 | 12' x 12' Green | 5 | 0 | 0 | 0 | 0 | 0 | PLEL
[6 empty] | Floor | Tile | Vinyl Tile | N | [6 empty] | S038 | 12' x 12' Green
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 12 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4011 | 4011 | Y | Office | 058 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4012 | 4012 | Y | Office | 059 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4013 | 4013 | Y | Office | 060 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4014 | 4014 | Y | Office | 061 | Floor | Tile | Vinyl Tile | NS | [6 empty] | VS012 | 12' x 12' Light grey with black streaks | [6 empty] | PLEL | NS as the material was visually similar to S012.
[6 empty] | Floor | Tile | Tile Mastic | NS | [6 empty] | VS012 | 12' x 12' Light grey with black streaks | [7 empty] | NS as the material was visually similar to S012.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4015 | 4015 | Y | Office | 062 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4016 | 4016 | Y | Office | 063 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4017 | 4017 | Y | Office | 064 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4000 | 4000 | Y | Office | 065 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4C01 |  | Y | Hallway | 066 | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS013 | Grey with light grey and white | [6 empty] | PLEL | NS as the material was visually the same as S013
[6 empty] | Floor | Sheet Flooring | VSF Mastic | P | D | N | SF | 800 | - | - | VS013 | Grey with light grey and white | 4 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually the same as S013.
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S040 | DWJC
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S041 | DWJC
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002..
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 4001 | 4001 | Y | Office | 067 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4002 | 4002 | Y | Office | 068 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4003 | 4003 | Y | Office | 069 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4004 | 4004 | Y | Office | 070 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4005 | 4005 | Y | Office | 071 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 4006 | 4006 | Y | Men's Washroom | 072 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F
J | 4007 | 4007 | Y | Women's Washroom | 073 | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as clay is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 275 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/f
J | 4010 | 4010 | Y | Office | 074 | Floor |  | Carpet | NS | [14 empty] | PLEL | NS as carpet is not suspect ACM.
[6 empty] | Wall | Drywall | DWJC | N | [6 empty] | S046 | DWJC
[6 empty] | Ceiling |  | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 1000 | 1000 | Y | Archive Room | 075 | Floor | Tile | Vinyl Tile | N | [6 empty] | S045 | 12' x 12' Blue with grey flecks | [6 empty] | PLEL
[6 empty] | Floor | Tile | Tile Mastic | N | [6 empty] | S045 | 12' x 12' Blue with grey flecks
[6 empty] | Wall | Drywall | DWJC | NS | [15 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | 9 | - | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | Ductwork | Parging Cement | P | D | Y | SF | 124 |  | 2 | VS026 | Parging debris | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S026.
[6 empty] | Other | N/F
J | 2001 | 2001 | Y | CLOSET | 002 | Floor | Tile | Tile mastic | P | D | N | SF | 8 | - | - | VS004 | Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as sample is similar to S004
[6 empty] | Floor | Tile | Vinyl tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as sample is similar to S004
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Mechanical | N/F
[6 empty] | Piping | N/F
[6 empty] | Other | N/F
J | 2000E | 2000 | Y | CLOSET | 004 | Floor | Concrete | Concrete | NS | [6 empty] | VS002 | Green VSF | [6 empty] | PLEL | NS as sample is similar to S002
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | WALL | Concrete | Concrete | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2013 | 2013 | Y | Office |  | Floor | Carpet | Carpet | NS | [6 empty] | VS005 | Grey with black streak | [6 empty] | PLEL | NS as material is simila to S005
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as DWJC was sampled in a representative # of locations.
[6 empty] | Wall | Fixed | Plaster | P | A | N | SF | 150 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as sample is similar to S002
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2E01, 3E01, 4E01, 1E01 |  | Y | ELEV |  | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS035 | BEIGE SHEET FLOORING | [6 empty] | PLEL | NS as sample is similar to S035
[6 empty] | Wall |  | Steel | NS | [15 empty] | NS as DWJC was sampled in a representative # of locations.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2015 | 2015 | Y |  |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling |  | Steel | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 3006 | 3006 | Y | LUNCH ROOM |  | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 100 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 3004 | 3004 | Y |  |  | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 300 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 3011 | 3011 | Y | closet |  | Floor | Tile | Clay | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 20 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2C02, 2CO2A |  | Y | Hallway | 014 | Floor | Sheet Flooring | Vinyl Mastic | P | D | N | SF | 500 | - | - | VS013 | Mastic - grey with grey and white flecks | 4 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S013.
[6 empty] | Floor | Sheet Flooring | VSF | NS | [6 empty] | VS013 | Light grey with grey and white flecks | [7 empty] | NS as the material was visually similar to S013.
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | D | Y | EA | 30 | - | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Piping | Elbows/Fittings | Tar mastic | NS | [6 empty] | VS005 | Tar mastic | [7 empty] | NS as the material was visually similar to S005.
[6 empty] | Piping | Straight Run | Tar paper | NS | [6 empty] | VS006 | Tar paper | [7 empty] | NS as the material was visually similar to S006.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2009, 2009A, 2009B | 2009 | Y | Office | 020 | Floor | Tile | Tile mastic | P | D | N | SF | 340 | - | - | VS004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002.
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | - | 10 | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | A | Y | EA | - | 1 | 1 | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 2023 | 2023 | Y | Hallway | 025 | Floor | Carpet | Carpet | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall | Drywall | DWJC | NS | [6 empty] | VS017 | DWJC | [7 empty] | NS as a representative amount of DWJC was sampled in other locations.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually the same as S002
[6 empty] | Piping | Elbows/Fittings | Tar mastic | NS | [6 empty] | VS005 | Tar mastic | [7 empty] | NS as the material was visually similar to S005.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 1S01, 2S01, 3S01, 4S01 |  | Y | Stairwell | 031 | Floor | Tile | Tile mastic | P | D | N | SF | 20 | - | - | VS004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl tile | NS | [6 empty] | VS012 | 12' x 12' Light grey with black streaks | [7 empty] | NS as the material was visually similar to S012.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S010.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 1S02, 2S02, 3S02, 4S02 |  | Y | Stairwell | 031 | Floor | Tile | Tile mastic | P | D | N | SF | 125 | 0 | 0 | VS004 | 12' x 12' Mastic - white with abundant brown fleck | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl tile | NS | [6 empty] | VS004 | 12' x 12' White with abundant brown flecks | [7 empty] | NS as the material was visually similar to S004.
[6 empty] | Floor | Tile | Vinyl tile | Y | A | N | SF | 210 | - | - | S024 | 9' x 9' Brown with brown streak | 5 | 0 | 0 | 0 | 0 | 0 |  | Insufficient mastic to analyze.
[6 empty] | Wall | Fixed | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | Ductwork | Parging cement | Y | D | Y | SF | 63 | - | - | S026 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | N/F
J | 1S03, 2S03 |  | Y | Stairwell | 032 | Floor | Tile | Vinyl tile | P | A | N | SF | 4 | - | - | VS023 | 9' x 9' Brown with thick black streak | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as the material was visually similar to S023.
[6 empty] | Floor | Tile | Tile Mastic | P | D | N | SF | 4 | - | - | VS023 | 9' x 9' Brown with thick black streak | 3 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S023.
[6 empty] | Floor | Tile | Vinyl tile | P | A | N | SF | 150 | - | - | VS024 | 9' x 9' Brown with brown streaks | 5 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S024. Insufficient mastic to analyze.
[6 empty] | Floor | Tile | Vinyl tile | N | [6 empty] | S027 | 12' x 12' Brown with abundant brown
[6 empty] | Floor | Tile | Tile Mastic | N | [6 empty] | S027 | 12' x 12' Brown with abundant brown
[6 empty] | Wall | Fixed | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 130 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/f
J | 1C01 |  | Y | Hallway | 033 | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as concrete is not suspect ACM.
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Acoustic tile | Lay-in T-bar | NS | [6 empty] | VS002 | 2' x 2' pinhole fissure | [7 empty] | NS as the material was visually similar to S002.
[6 empty] | Piping | Elbows/Fittings | Parging cement | P | A | Y | EA | 30 | - | - | VS003 | Parging cement | 30 | 0 | 0 | 0 | 0 | 0 |  | NS as the material was visually similar to S003.
[6 empty] | Mechanical | N/F
[6 empty] | Other | N/F
J | 3017 | 3017 | Y | ELECT ROOM | 057 | Floor | Tile | Tile mastic | Y | D | N | SF | 12 | - | - | VS038 | 12' x 12' Green | 5 | 0 | 0 | 0 | 0 | 0 | PLEL | NS as sample is similar to S038
[6 empty] | Floor | Tile | Vinyl tile | NS | [6 empty] | VS038 | 12' x 12' Green | [7 empty] | NS as sample is similar to S038
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as concrete is not suspect ACM.
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 12 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [17 empty] | No access above ceiling.
[6 empty] | Mechanical | N/F | [17 empty] | No access above ceiling.
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 1001 | 1001 | Y | MECH ROOM |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | Fittings | [9 empty] | New pipe fittings | [7 empty] | No access above ceiling.
[6 empty] | Mechanical | Tank | Parging | Y | C | Y | SF | 122 | 2 |  | S047 | Parging - tank insulation | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.
J | 1002 | 1002 | Y | ELECT ROOM |  | Floor | Concrete | Concrete | NS | [14 empty] | PLEL | NS as material is non suspect ACM
[6 empty] | Wall | Concrete | Concrete | NS | [15 empty] | NS as material is non suspect ACM
[6 empty] | Ceiling | Fixed | Plaster | P | A | N | SF | 200 | - | - | VS010 | Plaster | 2 | 0 | 0 | 0 | 0 | 0 |  | The base layer of S010 was ACM; therefore all plaster is considered ACM.
[6 empty] | Piping | N/F | [9 empty] | not insulated | [7 empty] | No access above ceiling.
[6 empty] | Mechanical |  | Parging | Y | C | Y | SF | 130 |  |  | VS047 | PARGING | 30 | 0 | 0 | 0 | 0 | 0
[6 empty] | Other | N/F | [17 empty] | No access above ceiling.